REACTIVE POWER COMPENSATION AND LOAD FREQUENCY CONTROL OF GRID CONNECTED MICRO GRID SYSTEM USING STATIC VAR COMPENSATOR (CASE STUDY: DILLA SUBSTATION)

A THESIS SUBMITTED

IN PARTIAL FULFILLMENT OF THE REQUIREMENTS

FOR THE DEGREE OF

MASTER OF SCIENCE

In

POWER SYSTEM AND ENERGY ENGINEERING

By

KUMILACHEW CHANE

HAWASSA UNIVERSITY

HAWASSA UNIVERSITY INSTITUTE OF TECHNOLOGY

SCHOOL OF ELECTRICAL AND COMPUTER ENGINEERING

HAWASSA (ETHIOPIA)

SEPTEMBER 2021

REACTIVE POWER COMPENSATION AND LOAD FREQUENCY CONTROL OF GRID CONNECTED MICRO GRID SYSTEM USING STATIC VAR COMPENSATOR (CASE STUDY: DILLA SUBSTATION)

By

Kumilachew chane

A thesis submitted to Hawassa University, institute of technology, school of graduate studies, for the partial fulfillment of the requirement for the degree of masters of Science in power system and energy engineering.

ADVISOR: Dr. Bassem .K

CO- ADVISOR: Mr. Isayas. G

Hawassa, Ethiopia

SEPTEMBER 2021

# Declaration

I, the undersigned, declare that the thesis comprises my own work. In compliance with internationally accepted practices, I have acknowledged and refereed all materials used in this work. I know that non-adherence to the principles of academic honesty and integrity, misrepresentation/fabrication of any idea/data/fact/source will constitute sufficient ground for disciplinary action by the University and can evoke penal action from the sources, which have not properly cited or acknowledged.

Kumilachew chane                                                     ________________

Student’s Name                                                                signature

Place: Hawassa institute of technology, Hawassa University, Hawassa

Date of submission ________________________

This thesis have submitted for examination with my approval as a university advisor

Dr. Bassem .K                                                                         __________

Advisor Name                                                                        signature

Mr. Isayas. G                                                                             ___________

Co-Advisor                                                                                   signature

Acknowledgement

First of all, I would like to thank the Almighty of  God for his endless support  For the completion of this work.

It is my proud privilege to express my deepest gratitude and admiration to my Advisors Dr. Baseem Khan and Mr.Isayas G. for their good guidance and support,

I wish to give my sincere thanks to ECE power staff members and Ethiopian electric utility office HAWASSA branch SNNP metrology agency office for their help when I collect the data.

HAWASSA UNIVERSITY

INSTITUTE OF TECHNOLOGY

SCHOOL OF RESEARCH AND POSTGRADUATE STUDIES

FACULTY OF ELECTRICAL AND COMPUTER ENGINEERING

ADVISOR’S APPROVAL SHEET ONE

This is to certify that the thesis entitled “REACTIVE POWER COMPENSATION AND LOAD FREQUENCY CONTROL OF GRID CONNECTED MICRO GRID SYSTEM USING STATIC VAR COMPENSATOR (CASE STUDY: DILLA SUBSTATION)’’ submitted in partial fulﬁllment of the requirements for the degree of Masters of Science in Electrical Engineering with specialization in “POWER SYSTEM AND ENERGY ENGINEERING”. The Graduate Program of the Department of Electrical and Computer Engineering, and carried out by kumilachew chane ID No- PGPSER/0005/11, under my supervision. Therefore, I recommend that the student has fulﬁlled the requirements and hence hereby can submit the thesis to the department.

Dr. Bassem.K                                            ___________                        _____________

Major Advisor                                               signature                                   Date

Mr. Isayas. G                                              ___________                        ______________

Co-Advisor                                                      signature                                   Date

Contents

CHAPTER ONE	1

Introduction	1

1.1 General	1

1.1.1Reactive Power compensation in the grid connected system	3

1.1.2 Basic principle of reactive power compensation	5

1.2 Statement of problem	5

1.3 Objectives	6

1.3.1General objective	6

1.3.2 Specific objectives	6

1.4 Scope of the thesis	6

1.5   Significance of the thesis	6

1.6 Methodology	7

1.7 organization of the thesis	8

CHAPTER TWO	9

LITRETURE RIVEW	9

2.1 Introduction	9

2.2 MICROGRID COMPONENTS AND FORMATION	12

2.3 METHOD USED FOR REACTIVE POWER COMPENSATION	14

2.4 Static VAR Compensators (SVCs) for reactive power compensation	15

2.5  Need of Reactive Power Compensation	17

CHAPTER THREE	19

METHODOLOGY	19

3.1General work flow of the thesis	19

3.2 The proposed System Model	20

3.3 MAIN GRID POWER  FLOW AND RATING	21

3.3.1reactive Power Varation In The Syetem	24

3.4 Frequency control	30

3.4.1Automatic load Frequency control	32

3.4.2 Designing   and Mathematical formulation of   SSILFC( frequency controlling)	32

3.5 Modeling and sizing of PV System	34

3.5.1 Sizing the solar array	34

3.5.2 Sizing of the Battery	36

3.5.3 Sizing of the charge Controller	37

3.6 Mathematical formulation of SVC	39

3.6.1Thyristor control reactor (TCR-FC)	40

3.6.2OPERATING PRINCIPLE OF  TCR-FC based SVC	42

3.7 Neural network	43

3.8 Problem Formulation	47

3.8.1 objective   function and constrint   condtions	47

3.8 .2)Minimize Var Cost and Real Power Losses	48

CHAPTER -4	50

4.  RESULT AND DISCUSSION	50

4.1 Result	50

4.2 Grid connected system during peak load condition	52

4.3GRID CONNECTED MICRO GRID SYSTEM DURING CONTINGENCY	54

4.3 STATIC VAR COMPENSETOR (SVC) with TCR-FC	56

4.4 LOAD FREQUENCY CONTROLLE	57

4.5 Grid connected micro grid system with controlling system	58

4.6 Power Loss & cost minimization	64

4.6.1Cost analysis of the real power loss in the GCMG system	67

Chapter five	71

5. Conclusions and recommendation	71

5.1Conclusions	71

5.2Recommendation	72

5.3 Future work	72

Reference	73

APPENDIX	77

List of figure

Figure1.1block diagram for methodology arrangement	7

Figure 2.1Configuration of grid connected a micro grid system	13

Figure 3.1 work flow by flow chart of the thesis	19

Figure 3.2 grid connected micro grid proposed model	20

Figure 3.3grid connected Micro gird configuration model	21

Figure 3.4 Single line diagram of the DILLA sub station………………………………………...22

Figure 3.5 Fig a) the graphical representation and b) the bar graph representation	25

Figure 3.6 Fig a) graphical representation of VAR fluctuation b) bar graph representation of VAR fluctuation	25

Figure 3.7  V,I  representation  during  contingency conditions of DILLA	27

Figure 3.8 representation of real and reactive power variation before contingency	29

Figure 3.9 real and reactive power fluctuation during contingency condition	29

Figure 3.10 block diagram of proposed frequency controller loop…………...…………………..30

Figure 3.11 integral control of load frequency…………………………………………………..32

Figure 3.12block digram of grid connected PV system 	33

Figure 3.13 circiut diagram of the grid connected PV system configration………………...…………….38

Figure 3.14: TCR-FC Equivalent circuit and Circuit diagram of TCR	.….39

Figure 3.15graphical representation of TCR-FC opreation	40

Figure 3.16 Flow chart of operation of ANN	44

Figure 3.17 ANN Architecture including different layer ……………………………………………….…...44

Figure 4.1simulation of grid connected micro grid load flow and feeder arrangement by ETAP	51

Figure 4.2Simulink diagram for grid connected micro grid system during peak load	52

Figure 4.3 Simulink of active and reactive power of GCMGS	53

Figure 4.4Simulink graph of Active power for peak load condition	53

Figure 4.5Simulink of GCMG system during contingency condition	54

Figure 4.6of Simulink result of active and reactive power flow of GCMG during contingency condition	55

Figure 4.7of Simulink result of voltage disturbance during contingency condition	55

Figure 4.8Voltage and current disturbance during contingency condition	56

Figure 4.9of Simulink diagram for of thyristor control reactor with fixed capacitor of SVC	56

Figure 4.10of Simulink diagram of load frequency controller with integral controller	57

Figure 4.12Simulink of GCMG system reactive power compensation by ANN of SVC	58

Figure 4.13Simulink of active and reactive power after compensation process	59

Figure 4.14Simulink result of Active and reactive power after compensation	60

Figure 4.15reactive power flow of based on artificial neural network controlled SVC	60

Figure 4.16active power flow of the based on artificial neural network controlled SVC	60

Figure 4.17 graphical representation of improved active power of the GCMG system in variable load	61

Figur 4.18 Comparative of ANN with FUZZY and MOFA based SVC…………….……………………71

Figure 4.19 power factor improvement graph……………………………………………………...73

List of table

| Table2.1 Table3.1 | Comparision of different implemented divice…………….…….. …….…………………….17 The main grid station of DILLA during peak load condition ……..…….……30 |
| --- | --- |
| Table3.2 | Max, min and average recorded value during peak load …………………. 32 |
| Table3.3 | Average recorded value of during contingency condition ……………...... 34 |
| Table 3.4 | Real and reactive power variations before and after contingency ……..…...36 |
| Table3.5 | Average temperature and solar radiation data ……. ……………………… 39 |
| Table 4.1 Table 4.2 Table 4.3 | Compression analysis of with and without SVC….……………………….….. 69 Comparission of ANN,FUZZY and MOFA controller ………..……….………….71 Total annual power loss in birr with and with out SVC……………………..74 |

List of acronyms

| AFDR | actual feeder rat of day |
| --- | --- |
| AI | artificial interagency |
| ANN | artificial neural network |
| CRPC | central reactive power compensation |
| DF | disturbance frequency |
| DRPC | decentralized reactive power compensation |
| ES | expert system |
| FC | harmonic filter |
| FDR | feeder rat of day |
| FI | frequency interruption |
| FT | fuzzy theory |
| GCMG LFC | grid connected micro grid load frequency control |
| LFC | load frequency control |
| MG MOFA | micro grid multi objective fire flow algorithm |
| MSC | capacitor bank |
| MSR | inductor bank |
| PCC | point of common coupling |
| PV | photo voltaic |
| QS | Quality service |
| RPC | point of common coupling |
| SVC | static VAR compensator |
| TCR | thyristor control reactor |
| TCR-FC | thyristor control reactor with fixed capacitor |
| TSC | thyristor switched controller |
| TG | wind turbine generator |

ABSTRACT

In the modern power system, reactive power compensation and load frequency control are two of the main issues. The aim of this thesis is to study reactive power compensation and load frequency control of the grid-connected micro grid system (GCMG) under variable load .In this work, an Artificial Neural Network based Static VAR compensator (ANN-SVC) and Load Frequency Controller (LFC) will be proposed for reactive power compensation and load frequency control of the grid-connected micro grid system, The artificial neural network (ANN) is used to control the the SVC gete signal for proper controlling of the thyristor valve in  the circulated  system current management.   Power system Planning and management provide the strategy for reactive power compensation and load frequency disturbance control. The ANN-controlled SVC is used for managing and compensating of reactive power in the system and LFCis control the system load frequency disturbance and the LFC controlling loop component  is control  and managed by ANN signal for proper controlling of the load frequency error.  The real and reactive powers before applying the SVC at the peak load conditions are 40.56MW and 27.16MVAr, respectively, before reactive power compensation. During contingency conditions, the real and reactive powers are 36.03MW and 30.42MVAr, respectively, and the frequency is highly disturbed for a fraction of a second, but after compensation, the real power is improved to 50.54MW, while the reactive power is reduced to 17.34MVAr. Therefore, real power is improved by 52.18% while reactive power is compensated by 87.02%. The steady-state load frequency error is reduced by 95%, while the system power factor is improved by 94%. A detailed comparative analysis of the proposed ANN-based SVC with the fuzzy-based and multi-objective fire fly (MOFA) algorithm SVC is presented, which shows that the ANN-based SVC has better performance, fast and accuracy, in case of the above justification ANN is more prifereble than MOFA and FUZZY algorithem. The general GCMG structure with the compensation and controlling process was designed by ETAP and MATLAB/Simulink

Key word    Static VAR compensator (SVC), Thyristor Control Reactor for Fixed Capacitor (TCR-FC), Artificial Neural Network (ANN), Grid Connected Micro Grid System (GCMG)

# CHAPTER ONE

# Introduction

## 1.1 General

Reactive power (VAR) compensation is demarcated as the management of reactive power to improve the performance of the ac power system. Reactive power can best be defined as the quantity of idle power that is developed by reactive components such as inductors or capacitors. Reactive power is necessary to move active power through the transmission and distribution system to the customer. Power factor correction is one of the best investments to reduce energy costs with a short payback in [1].

Reactive power is important in the power system operation in different situations. If the voltage on the system is small, active power cannot be supplied. Reactive power is used to provide the voltage ranks essential for active power to do suitable work. Reactive power is essential to move active power through the transmission and distribution system to the customer by different methods in the power system controlling and voltage maintaining strategy. Reactive power compensation scheduling provides the opportunity of power loss reduction and voltage profile improvement for the network operator. Herein, capacitor banks and other electronic components are widely incorporated for reactive power compensation in electric power systems because of their more economic justifiably than series VAR compensation. There are two important factors in reactive power compensation, including demand power and the optimal deployment of installed capacitor banks in the case of different operation modes. Optimal reactive power control of power systems can lead to minimal active power loss, improved voltage profile, and minimization of the cost of reactive power generation. Micro grid refers to a low voltage generation and distribution network that includes small-scale generation sources, energy storage devices, controllable and uncontrollable loads, local controllers, a central controller as well as telecommunication system micro grids are small-scale versions of standard grids. They supply nearby produced energy openly to a group of users. MGs are generally joined to the main grid, while in emergency situations they may operate in is landed mode. Hence, it is deliberated as active flexible cells in an electric power system. Different Renewable energy are being connected to power systems worldwide in large numbers. As a result of the intermittent nature of these sources, in addition to the steadily increasing overall load demand, electricity systems currently are faced with many challenges in security and operational reliability. With modern advanced grid-integration methods, these energy resources are empowered to become reactive power sources. effective Reactive power management should address three basic requirements in the power system.To maintain voltage within predefined limits, it seeks to minimize congestion of real power flows and, it seeks to minimize power losses. Load Frequency Control (LFC) is a system to keep wisely constant frequency to load between the generators and to control the tie-line interchange schedules. Load Frequency Control is seriously needed for power system because of the quality of power. Load frequency control (LFC) in power system maintains frequency deviation & tie-line power flow deviation. Load frequency control is the basis of many advanced concepts of the large scale control of the power system. There are two kinds of power in an AC power stream reactive power and active power (real or true power). Reactive power is moved from the source to the load and then returns from the load to the source, then the average power supplied is zero. Reactive power compensation is required to keep the system voltage within the appropriate limit. According to speed and capacity to absorb or produce reactive power, can be classified as dynamic and static. Reactive Power is less exposed to competitive mechanisms.it is one kind of ancillary service that system operators need to procure to maintain network stability within the right voltage limits in [2].

The power system operates on an AC system and most of the loads used in our daily life demand reactive power. Thus reactive power or VAR compensation is described as the management of reactive energy to increase the routine of the AC system. The subject of reactive power compensation is realized in two ways: load and voltage support. The aim is to attain a better-quality power factor and real power balance from the load point of view. Reactive power generation has been normally used voltage profile enhancement in power systems. However, the opportunity price of reactive power generation should be measured. since it affects the frequency control capability of the system in [3].  Active power is necessary for running of any type of the electrical load. To transmit this active power from generation to the electrical loads, Reactive power is necessary to adjusts the voltage level of  system. If voltage of the system is not sufficient, essential active power cannot be supplied. So reactive power is used to maintain the enough voltage for active power to do useful work in [4].

Our power system operates on an AC system and most of the loads used in our daily life are inductive in nature which requires reactive power. Additional reactive power requirement is observed at the load side to maintain voltage profile or power factor improvement. In general, the problem of reactive power compensation is seen from two facets: load compensation and voltage support. In load compensation, the goals are to increase the system power factor, to balance the real power drawn. Voltage support is generally required to reduce voltage fluctuation at a given terminal of a transmission/distribution line. In both cases, the reactive power that movements through the system can be successfully controlled. Reactive power compensation in power systems also improves the stability of the ac system by increasing the maximum active power that can be transmitted in[5].

Reactive power compensation by suitable means has developed the most economically pretty and effective solution technically for both traditional and new problems at different voltage levels in a power system. VAR compensation near load center has gained more importance in recent times in [6].

### 1.1.1Reactive Power compensation in the grid connected system

In order to agitate the realities of electrical energy and dynamical energy methods, planners confirm to place voltage management measures .The voltage is often management led by providing reactive power control margin to modulate the provision wants through the subsequent compensations as given below.

a. Series compensation.

b. Shunt compensation.

c.. Dynamic compensator.

These classes square measure primarily supported the strategies of connecting the capacitance bank with the system. Series and Shunt volt-ampere compensation techniques square measure accustomed modify the natural electrical characteristics of electrical facility.

#### 1.1.1 a) SERIES COMPENSATION

Series capacitors on the opposite hand haven't any management over the flow of current. As these square measure connected serial with the load, the load current perpetually passes through the series capacitance bank. The voltage regulation of the system is improved. Therefore series capacitance should have refined and elaborate protecting instrumentality.

There square measure some specific benefits of victimization sires capacitors (SCB) like,

- It reduces the road current of the system.

- It improves the voltage level of the load.

- It conjointly reduces system Losses.

- It improves the ability issue of the supply current.

- It reduces the load of the generator.

#### 1.1.1  b)Shunt compensation.

Shunt capacitance is connected, which attracts current resulting in the supply voltage A shunt capacitance attracts virtually fastened quantity of leading current that is superimposed on the load current and consequently reduces reactive parts of the load and therefore improves the ability issue of the system. Moreover, capacitance banks that square measure put in in load points with low demanded power square measure unable to share their excess capability with load points than have a high demanded power.

#### 1.1.1 c) Dynamic compensation

The dynamic reactive compensation is to share the compensation characteristic of the shunt system and series compensation system They will be utilized in single-phase or three-phase systems, in substations, on the distribution lines or at the doorway of a selected client. We can distinguish the subsequent styles of reactive power in the dynamic mejore.

- Shifting reactive power: caused by inductive and/or electrical phenomenon masses. These guarantee current ‘lags/runs late’ behind the voltage

- Distortive reactive power: this is often the ‘unwanted’ a part of the apparent power related to harmonic pollution caused by non-linear masses.

### 1.1.2 Basic principle of reactive power compensation

In the basic principle of the reactive power controlling and compensation process consists of three parts:

- Stratified by voltage,

- partition by the power grid and

- Local equilibrium.

Researchers have considered load regulation to obtain high energy efficiency for steady-state situations.. The system has been tested under resistive-inductive load without examining phase inequality in [16]. For this, an economic model predictive control has addressed in this study.

## 1.2 Statement of problem

The rate of electrification for the rural part of Ethiopia is less than three percent (3%), while 85 percent of the rural population is distributed in villages. Providing electricity access to such dispersed populations using different old electrification process but the government have a plan to construct different micro grid and improve the traditional micro grid until 2024 .In the GCMG system the micro grid is used to an additional source of  power in the grid integrated area when we connect the MG  system disturbance will be developed in the point of common connection(PCC) and around load. The main problems of the systems are

- Large amount of reactive power flow and real power loss.

- Voltage disturbance/ unbalanced voltage developed .

- Load frequency disturbance or variations  will be developed.

The micro grid will be  additional source to main grid system in the case study area  and  for the large amount of  reactive power flow and system load frequency disturbance management  different controlling method and technices  will be used  that is ANN based SVC and load frequency controller  will be used for the managing and controlling process of the reactive power and load frequency disturbance.The prime aim of the study in the Reactive Power Controlling or Management ( RPCM) and minimize the real power loss and  load frequency variation  as well as minimizing the expected total hourly voltage deviation of all load in the grid-connected micro grid.

## 1.3 Objectives

### 1.3.1General objective

To study reactive power compensation  and load  frequency control in grid connected micro grid system by using ANN control SVC and LFC in the MATLAB/ Simulink environment.

### 1.3.2 Specific objectives

- To study the existing system

- To Model  grid connected micro grid  system under variable load

- To develop  reactive power compensation mechanism by ANN controlled SVC

- Control  load frequency disturbance  (LFC) using LFC.

- Compare the ANN based SVC with FUZZY based SVC  and MOFA based SVC

## 1.4 Scope of the thesis

The thesis will be focus on reactive power management and frequency control by using  ANN based Static VAR Compensator (SVC) andload frequency control system.that are including real  power  loss and variation of reactive power flow that caused by sudden disturbance, the peoduced power from the MG are used to additional source  of the grid in the case study  area.

## 1.5   Significance of the thesis

- Managing and Minimizing the reactive power in the system

- Minimizing of the real power loss

- Improving of active power of the system  and  the power factor

- Reduction of load frequency disturbance

- Ensure the security of electric power continuity and Reduce power shortage and real power loss cost.

## 1.6 Methodology

The methods employed to achieve the objectives of this thesis are:

Figure 1. work flow for methodology arrangement

Under the topic called literature review the work of different authors; articles, journals, books, thesis done in similar topics and others have been reviewed and it has been considered one of the methodology used to do this Thesis. The total task of data collection is accomplished through

- Conducting interviews with the respective personnel of the case study area

- Direct measurement From recorded data and equipment specifications

- Physical observation (filed study) in the substations.

- Data from Ethiopian Electric Utility (EEU) engineering offices SNNPREEU

Computer analysis or Simulation There are different types of software which can be applicable on electrical power controlling for frequency and reactive power  simulation Power world, PSS, MAT-LAB,ETAP, PSO and Dig SILENT. From software mentioned above the MAT-LAB, ETAP is most recent, highly compatible and combined reliability and flexible system. The data is organized using EXCEL sheet and the single layout diagram and analysis using Power Factory Software the preferable solution.

Data analysis: Analysis has been done using power software load profile and different mechanism. Comparison has been done between the systems with SCB compensation, with the SVC during fault and peak load condition.

## 1.7 organization of the thesis

This thesis work is organized as in following chapters:-

In Chapter one presents about the introduction and background of the study, briefs about reactive power, statement of the problem, describes the objective of the thesis work and scope of the project.

In Chapter two describes about reactive power. It provides brief understanding of GCMG system, about micro grid, controlling and comparison about different technics.

In Chapter three   methodologies about the research and its proposed model, presents a literature review of other related works that has been done for both general power system and grid connected system. A brief discussion on active power  controlling mechanisms , mathematical model of micro grid (PV system  and battery ) ,load frequency  controller   and working principle and definition of ANN. reduction and reactive power compensation techniques.

In Chapter four   present  result and discussion about the system of GCMG system  during normal  condition , peak lead condition  and during contingency  condition  and loss and cost calculation presents the  ETAP  and MATLAB/SIMULINK modeling, simulation results and analysis of the reactive power consumption in different cases for GCMG  power network with and without SVC .

In Chapter five  the conclusions and recommendation of this research work can be found. Moreover, some suggestions on the extensions to potential topics for future research are presented.

# CHAPTER TWO

# LITRETURE RIVEW

## 2.1 Introduction

The aim of this chapter is to critically review of many research works which are more related to this work, in order to have a clear understanding of the subject matter.  In this part we will try to study the different grid connected micro grid system in the reactive power compensation and micro grid power plant are presented for the power generation perpuse. In addition to this, Reactive power  compensation method , component that are used to reactive power compensation ,the main components of micro grid connected grid system , the components that are used to synchronize the MG to the grid are  studied and discussed based on the different scholars idea  and document  as well as brief experiment. We always  in applied to  reduce reactive power to improve system competence .this is acceptable  at same level  if the system is purely resistive  it make Couse same problem  in electrical system.

Voltage and reactive power is closely related to the maintenance of the voltage level of the whole system, it must have sufficient reactive power to meet the system load demand for reactive power and reactive power compensation of losses and voltage control of power systems are mainly by controlling the reactive power generation, flow and consumption to achieve.

Reactive  power  controlling  has  become  a  most  interesting  task  in  power  system  operation  and management. Some of the characteristics of the power systems and their loads can deteriorate the quality of the  power supply in [1].

In the power scheme, reactive power should be maintained stable, or otherwise, it would worsen the system voltage, and even cause the voltage collapse accidents. Therefore, the optimized and recompense of the grid system have abundant significance to improving the voltage quality, power factor and the efficiency of the power supply. It is also suitable to reduce the system losses. It is a foremost energy saving technical measure with small investment and quick returns in [3].

For this reason it can be compensated by VAR producers, avoiding its circulation between the load (inductive or capacitive) and the source, and therefore improving voltage stability of the power system. Load compensation is the controlling of the reactive power to increase the quality of the supplying ac power systems.  Reactive power compensation can be implemented with VAR generators connected in parallel or in series in[4].

A reactor or a capacitor stores the reactive power produced by the ac power source during a single operation. In other words, the reactive  power fluctuates among the source and the load at a frequency equal to twice the rated charge. However  in  nature,  most  of  the  loads  are  inductive loads  absorbing  reactive  power  and  resulting  in  low lagging power factor in [6]

A Micro-grid could be defined as a low-voltage distribution network .Generally speaking, Micro-grid could be operated in either grid-connected or islanding mode. Reactive power is organized the difficult and the solution to system voltage regulator. There are many authors and researchers who have worked voltage and reactive power control for power loss minimization using different techniques ’A network of low voltage power generating units, storage devices and loads capable of supplying a local area such as suburban area, an industry or any commercial area with electric power and heat’. The components of Micro grid are interfaced through quick response power electronics and present itself as a single entity and therefore can be connected to traditional power grid or can also be operated in stand-alone mode as a self-sustained power system in [7]

Transformers, asynchronous motors and different inductive component can absorb reactive power from the grid throughout their operation periods, which, to a particular extent, can cut back the system power issue. The reactive power demand will be salaried by reactive power compensation device that is useful to cut back the reactive power flow within the grid, cut back the electrical energy loss because of the delivery of reactive power, and successively, improve the operative condition of the grid. This development is termed reactive power compensation  in[8].

The basic principle of reactive power compensation consists of three parts: stratified by voltage, partition by the facility grid and native equilibrium. Within the installation, reactive power ought to be maintained balanced, or otherwise, it might worsen the system voltage, and even cause the voltage collapse accidents. Additionally, if the voltage is lower, it'll cut back instrumentation utilization and increase the real power loss. Therefore, the optimization and compensation of the grid system have nice significance to up the voltage quality, power issue and therefore the potency of the facility offer. it's additionally helpful to cut back the system losses. it's a foremost energy saving technical live with tiny investment and fast returns in[8].

Many researchers has done on reactive power composition or related to load characteristics to solve the problem with voltage stability done on management of dynamic reactive power reserves based on optimal power flow and the Bender’s decomposition technique to improve voltage stability.  Unbalanced system reaction for different load models and network situations by chalking Impact of Fault Locations on Induction Motor Responses, Impact of Fault Duration on Induction Motor Responses and impact of generator response in[9].

Reactive power compensation should be consisting of the compensation for both the fundamental wave reactive power and the disturbance of reactive power. Reactive power compensation play an important role in this current time because supplier /customer take charges of it, if it exceeds a predetermined value so different customer /companies enforce users to compensate it, and to reduce the power consumption. The consumer has to pay electricity charges for his maximum demand in kVA plus the unit consumed if the value of power factor is improved by the customer so there will be annual saving. Power factor improvement results increasing making capacity of plant.in[10].

Reactive Power Management is a critical issue when dealing with the planning and operation of power networks with high wind energy penetration. Reactive Power Management entails the requested operation and planning actions to be implemented in order to improve the voltage profile and the voltage stability in power networks.  An efficient reactive power planning could be obtained by choosing an optimum location of VAR sources during the planning stage, whereas efficient reactive power dispatch could be achieved by scheduling an optimum regulation of the voltage set point at the generators connection point and at the VAR settings during the reactive power dispatch in[11].

Reactive power compensation using power electronics, in this research he investigated the various fact device and he come up with the best compensator for ac system that is the shunt compensator. It gives a good line of regulation of the power transfer capability. SVC is a very good compensator for dynamic heavy electrical loads in[12].

The main thing is to reduce the reactive power flow so as result reducing the electrical energy charges. Most appropriate method for compensating reactive power flow is power capacitor, which is economical and efficient as well compare to filter and compensating by synchronous condenser. The capacitor bank to compensate the reactive power flow automatically, for that we will discuss single, group and bulk power factor correction techniques according to level of customer used but capacitor banking will be low efficiency and less reliable  in[13].

Reactive power compensation is one of the most effective ways to reduce Consumed electric energy and improve power quality. How reactive power compensation can improve the technical-and-economic indexes of the   power grid are as follows:

- reduce cost and generate higher revenue for the customer

- reduce network losses, increase system capacity and save costs on new installations

- improve system power factor and increase power availability

Same Electronic device  are used to improve and control the mini micro grid  level according to this  Any device which is connected in series or parallel with the  load  and  which  is  capable  of  supplying  reactive power  demand  to  the  load  is  called  reactive  power compensation device  in [14].

## 2.2 MICROGRID COMPONENTS AND FORMATION

The micro grid will be connected to the utility grid through single point of Common Coupling (PCC). The analytic device is employed to isolate the small grid from the utility grid A small grid integration of assorted units. Basically, it consists of metric weight unit energy-storage unit, controller unit and traditional load. The metric weight unit once more compromises of assorted micro-generating devices. Therefore, small grid modeling varies from one configuration to alternative looking on the parts used. varied approaches for the modeling and management of small grid will be found within the literature in[15]

The micro grid contain Meany mini micro grid sources

- PV (photo voltaic ) system

- Battery storage system

All mini micro grids have its own generating methods and generated component and its generating limit with respect to the selected location  and material or equipment rated value[16]. The PV system are mainly produce the DC power   but after production  or generation  of the DC power the DC-DC converter  to convert and transform the  DC input to  DC out  then the inverter are convert the dc input  to AC  output and  different researcher  are  to explain the micro grid component  and  its converter  without any controller and its smart communication midume in [12].

Figure 2.Configuration of grid connected a micro grid system

Solar power, an important renewable power, has been on the increase in most parts of the world in terms of installations .This is as a result of abundant sunlight shining on the earth from the sun every year and making conversion of this source to usable sustainable electric power a top priority for most developed and developing countries. A technology utilizing the principle of thermal power plants called concentrated solar power (CSP) or solar thermal (CST) is one of them The other technology uses the photovoltaic effect and is known as solar photovoltaic (PV) power in[17].but the controller and production limit will be  the drow back of the implemented system .

Wind is a renewable energy source and wind power generation means getting the electrical energy by converting wind energy into rotating energy of the blades and converting that rotating energy into electrical energy by the generator. Wind energy increases with the cube of the wind speed, therefore WTGs should be installed in the higher wind speed area in[18]

Wind power technology will contribute to the distribution system by control its active power output to boost the system responsibility. to boot, it may be economically helpful to enhance voltage quality similarly as load sharing with generation at varied times, avoiding load shedding and risk of potential blackouts. But when we study wind system thechallenge will be the out put of the generation is variable because the output of the generator is depend on wind speed and terbine activity so  we must understand when we use renewable source of micro grid parallaly develop and prepear the large energy storage divice.

## 2.3 METHOD USED FOR REACTIVE POWER COMPENSATION

Generally two methods are there for reactive power compensation.

A. Decentralized Method (DM)

In decentralized reactive power compensation, the individual controlling device is installed locally in the network. The optimal size of controlling device can be obtained and install it wherever it is required for different period of times.

B. Centralized Method (CM)

The entire individual controlling device installed in the network is centralized. This will use for maintaining bus voltages and power factors. Reactive power control units are used for central compensation .The current industry practice uses the decentralized method for reactive power compensation. In decentralized reactive power compensation, the individual controlling device is installed locally in the network. It is very costly and uneconomical to buy a controlling device and install it wherever it is required for different period of times in [19].

When I study the different researcher document all of the above mentioned studies introduced decentralized reactive power compensation (DRPC) system. Herein, the DRPC planning problems specify optimal locations and sizes of capacitor banks for a specific load profile of the grid connected micro grids. The optimal locations of capacitor banks might be changed along with variations of micro grid load profile. Herein, the capacitor banks should be allocated for each prospective load profile to optimally benefit from the installed capacitor banks. However, the location of capacitor banks cannot be changed because this action is neither economically nor technically justifiable in [20]

But know the DRPC method will be not advisable according to

- Economic aspect  and Technical constraint

- Flexibility  and reliability when I compered to centralized method

## The centralized method will be more advisable for grid connected micro grid system because of different point of view. Centralized reactive power compensation (CRPC) system can inject reactive power to different load points to improve the QoS level for  grid connected micro grids in [20]

## The objective function of the devised CRPC system is to minimize the expected total hourly cost of grid connected micro grid operation and voltage deviation of load points. Moreover, the uncertainties of the problem including the demanded power of micro grid, output power of renewable energy resources, and electricity price are considered in the proposed formulation to more comprehensively determine the optimal capacity of the CRPC system. the performance of the proposed CRPC system is compared with a DRPC system to evaluate the effectiveness of the proposed system in the methodology in[21].

During this context, there ar many energy generation ways to confirm high-quality energy provide from the cell unit to the demand-side. the most purpose of energy management is to supervise the facility exchange between generation unit associated an electrical grid. it's utilized to rearrange swish power exchange from the cell to grid/load or contrariwise in[22].

Hence, the energy management methods associated with grid integration is considerable for

(1) Improvement of energy qualification and the minimization of grid interferences

(2) Optimal energy supply,

(3) Sustainable and reliable operation.

## 2.4 Static VAR Compensators (SVCs) for reactive power compensation

SVC is ready to manage the voltage at a selected bus by activity or engrossing reactive power. The benefits of simplicity, low losses, low harmonics production and low price have created SVC to be used extensively compared to different  FACTS devices. SVC may be a shunt connected FACTS device whose output is often adjusted to exchange either capacitive or inductive currents to the connected system.This Current is Controlled to manage specific parameters of the power system (typically bus voltage). It is a variable electric resistance device wherever this through a reactor is controlled victimization back to back connected Thyristor valves. The Thyristor has been AN integral half in realizing the SVC and to modify management of its reactive power flow. It's used either as a switch or as a unceasingly controlled valve by dominant the firing angle. It ought to be noted that the SVC current can contain some harmonic content, one thing that wants attention within the style method in[17].Within the steady-state, to take care of a predefined level at a high voltage bus some steady-state management of voltage is provided by the SVC in [23].

Table 2.1 Comparision and observation  of different implemented  compensation divice

| Selected component | Implemented and application | Observation and Advantage | Disadvantage |
| --- | --- | --- | --- |
| Capacitor | Power system operation and reactive power compensation [16][20] | -reactive power compensation for a limited power flow -economical cheep | -it is old and raged when we compare to anther fact device -performance of voltage profile mentenance |
| SVC-TSC | Large power flow and reactive power compensation with voltage profile [23] | -it have good performance for compensation process - it is smart and modernized when we study CB | -It required single program for large load operation -it required Large stage of iteration |
| SVC-TCR | Reactive power compensation in the large power industry[29] | -it has well accuracy and performance in the power system operation and compensation process -more modernized and minimum time required for the convergence stage -it is more reliable, small and effective - | -Large power industry and less harmonic filtration process |

## 2.5   Need of Reactive Power Compensation

When I observe the reactive power and frequency the necessity for reactive power compensation can be divided into three basic classes:

i.) The necessity to preserve the stability of synchronous machines. We shall see that voltage control by reactive power compensation can have a positive stabilizing effect on the system during disturbances because the rotor angles of synchronous machines to change quickly. Both the transient stability and the dynamic stability of a system can improve. It is even possible with controlled compensators to drive voltages purposely out of their normal steady-state bounds for several seconds following a fault or other major disturbance to enhance the stabilizing influence still more.and the voltage profile will be improved with releted to frequency controlling process.

ii) The need to control voltage within suitable bounds about the preferred steady-state value to provide quality service to consumer loads. Following certain abrupt changes in the load, or in the network arrangement as a result of switching actions, it may be necessary to make a voltage improvement in as short a time as a few cycles of the power frequency. For other voltage disturbances, a improvement within a few seconds will suffice. Uncorrected voltage deviations, even if momentary,

iii) The need to adjust voltage profiles in the network to prevent Unnecessary flows of reactive power on transmission lines. To this end, reactive power compensation can be used to preserve transmission losses to a practical minimum. While the reactive compensation must be adjusted or changed intermittently to maintain minimum losses, the adjustments can be made fairly rarely with several minutes to effect the preferred change.

But different  researchers  are to  study reactive power compensation  by using capacitor  bank and load frequency disturbance by manual adjestemnt way.  in my observation reactive power  controlling  and compensation is highly important by using SVC than  capacitor bank and integeral load frequency controlling system is more efficient the manual system  because  the above new controlling method will be are  more reliable  and efficient  than old system    and it is modernized  and latest  than the privies  component but when we  see the cost of the  material capacitor bank is cheaper  than SVC  but  the reliability , flexibility , performance as well accuracy of controlling  and compensation SVC  are more than ather and  advisable.and the ANN-SVC in the reactive power  compenseation is more prifereble  and acceptable  when we study reactive power compenseation  process related to different researcher .the compenseation of reactive power  by ANN-SVC are fast and acuret  because the ANN controlled and order  the SVC fring angle  in the thyristor valve. In case of the thyristor valve  the circulated current in the TCR-FC based SVC are control properly. But  in the simple capacitor  and  anther  fact divice  is not good closeness and relation  to the ANN and ather aretificial intelegent controller famile  because the  simple capacitor and  same fact divec is not moderated and properly mached to  the controller.The load frequency controller  are more important to contro the disturbed frequency in the load terminal. And the LCF system component  is managed and controlled  the ANN controlling signal then the LCF system is control the steady state error  and frequency divation perfectly.

# CHAPTER THREE

# METHODOLOGY

For controlling the reactive power and  frequency, ANN based SVC and LFC system is proposed. The proposed system reduces the GCMG frequency deviation and reactive power  during  peak loads and contingencies. The micro grid is additional source of the system or the main grid and during the reactive power management  the system active power will be improved.In this thesis ANN controlled SVC and LFC  system for the analysis and study of the reactive power compensation and load frequency control.

## 3.1General work flow of the thesis

Figure 3.1of work flow by flow chart of the thesis

## 3.2 The proposed System Model

In the grid connected  micro grid system, the  proposed model of the  micro grid side include  different renewable energy generation source are photo voltic(PV)  the major  renewable  source to study  and model  in this  thesis.

Figure 3.2 grid connected micro grid proposed model

The proposed system include controlling block components that are used to compensate and control the reactive power and load frequency. the load frequency disturbance will be developed during the micro grid are connected to the main grid in the different situation around PCC (point of common coupling ) and load side. Static VAR Compensators (SVCs) are the most useful devices to control and compensate the dynamic reactive power at the integrated grid level. The methods that are used to control the reactive power in different power stage are decentralization method or Local secondary control and centralization method or grid central control (GCC).but centralization method is the most effective and advisable method in this thesis.

Figure 3.3 grid connected Micro gird configuration model

The control system includes ANN-based SVC and integral load frequency controllers that are used to controlling mechanisms of reactive power and load frequency  in the GCMG system. each mini grid connected micro grid has its Owen energy production, controlling mechanisms, and technic to including reactive power controlling , managing and frequency variation. We can to controlled the Voltages and reactive power by providing sufficient reactive power control margin to supply. When I develop / model the micro grid I will try to include the renewable part of the energy generation of the PV system. Each energy generation  system and stage  is designed with standard declaration of IEEE rule.

## 3.3 MAIN GRID POWER  FLOW AND RATING

In DILLA we have 132kv incoming TRAFFO or feeder that are connected from national main grid station and contain or included  five different rate  outgoing feeder  that are 33kv and 15KV the 15KV rate feeder  are used  around  DILLA and YIRGACHEFFE the rest feeder will be  transmit and distribute energy to SOLLOMO and GOLOLCHA  city  line station.

Fig 3.4 single line diagram of dilla substation

Table3.1 of the main grid station of DILLA during peak load condition

| Feeder name | Feeder rate | Active power | Reactive power | Cf |
| --- | --- | --- | --- | --- |
| DILLA -1 | 15KV | 5424.000KW | 2394.000KVAR | 0.66 |
| DILLA -2 | 15KV | 5424.000KW | 2394.000KVAR | 0.66 |
| YIRGA CHEFFE | 15KV | 5424.000KW | 2394.000KVAR | 0.66 |
| SOLOMO | 33KV | 6550.500KW | 3399.000KVAR | 0.66 |
| GOLOLCHA | 33KV | 6550.500KW | 3399.000KVAR | 0.66 |

Active power per month for the 15KV feeder loads

In the system we have three 15KV feeders    that has totally 45KV rate

5424000KW =5424000/1000

= 5424 MW

Individual feeder rate in MW

= 5424/3=1808MW

Feeder rate per day will be   FRD

FRD=FRdayofthemonth     =FR30DAY                                             3.1

=60.266MW

The FDR value are   ideal power until the FDR value are mix with the total station feeder consistence constant Cf and the actual FDR is AFDR that is

AFDR= FDR*Cf                                                            3.2

=39.78MW

The reactive power will be of the 15KW feeder load

=2394MVAR

Individual feeder rate in MVAR = 2394/3=798MVAR

Feeder rate per day will be   FRD

FRD=FRdayofthemonth     =FR30DAY                                             3.3

=26.66MVAR

Total flow of reactive power in the system during peak load condition

28% RP+RP

= (26.66+7.9) MVAR= 33.16MVAR

The total frequency interruption of the 132KV grid line station system 273.19.

The total frequency interruption FI per second will be

FI=TFC/60s

4.55

The normal variation will be 5% the normal frequency in both side of the regular value that means 2.5 of the left and right. And the nominal frequency Nf will be constant

Disturbance on frequency will be Df

Df=Nf-FI                                                                    3.4

45.45

At the left side 45.45 and 54.55 at the right Based on the recorded and give information the system has frequency disturbance problem during peak load  and contingency conditions.

### 3.3.1REACTIVE POWER VARATION IN THE SYETEM

For the power grid  and micro grid power flow will be vary  time to time  according to the power flow and demand requirement of  the system  voltage and required of electric demand   the Reactive power  will be  vary  within time to time. Show the fluctuation of reactive power as well as the required limit of reactive power in the system.

Table3.2 of max, min and average recorded value of current, active and reactive power during peak load condition

| Time In H | line arrangement and rate | Average current during peak load condition (KA) |  |  | Average reactive power during peak load condition (Mvar) |  |  | Average power during peak load condition (MW) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Short | Bay | Max | Min | Average | Maxll | Min ave | Average | Max | Min | Avera |
| All | 132/15 TR1 | 1730 | 1655 | 1692 | 37 | 21 | 29 | 6.4 | 5.6 | 9.0 |
| All | 132/15 TR 2 | 1940 | 1502 | 1615 | 33.12 | 22.43 | 27.8 | 6.34 | 5.59 | 8.85 |
| 1 | Line 1/line 3 | 394/350 | 230/245 | 312/298 | 67/41 | 4.1/2.2 | 6.4/21 | 10.3 | 8.9 | 9.6 |
| 2 | Line2/line3 | 620/452 | 389/380 | 504/416 | 53/31 | 3.8/2.46 | 4.1/24 | 10.8 | 9.9 | 10.35 |
| 3 | Line 3/line 2 | 550/453 | 453/398 | 502/426 | 41/19 | 3.9/2.18 | 3.5/19 | 12.1 | 10.2 | 11.15 |
| 4 | Line 1/line3 | 434/390 | 344/320 | 389/355 | 43/23 | 2.7/2.21 | 3.5/17 | 12.0 | 11.1 | 11.55 |
| 5 | Line 2/line 1 | 389/390 | 280/230 | 335/310 | 34/23 | 3.9/2.3 | 3.7/18 | 12.8 | 10.1 | 11.45 |
| 6 | Line 5/line3 | 430/395 | 342/321 | 386/358 | 38/27 | 3.4/2.5 | 3.1/21 | 8.48 | 7.83 | 8.155 |
| 7 | Line2/line 5 | 453/345 | 231/301 | 342/323 | 40/19 | 3.8/2.1 | 3.4/15 | 7.95 | 7.74 | 7.845 |
| 8 | Line2/line3 | 542/580 | 230/299 | 386/440 | 42/29 | 2.4/2.0 | 3.3/29 | 9.07 | 8.1 | 8.585 |
| 9 | Line5/line 1 | 280/394 | 180/167 | 230/281 | 39/33 | 3.1/2.12 | 3.5/25 | 10.3 | 9.17 | 9.735 |
| 10 | Line 2/line3 | 467/380 | 420/321 | 444/351 | 38/21 | 2.93/2.1 | 4.1/15 | 11.4 | 9.75 | 10.575 |
| 11 | Line 2/line4 | 450/354 | 430/234 | 440/294 | 39/26 | 2.7/1.4 | 3.3/20 | 9.8 | 8.73 | 9.265 |
| 12 | Line 1/line4 | 357/399 | 245/321 | 301/360 | 41/29 | 2.8/1.9 | 3.9/19 | 10.3 | 7.95 | 9.125 |

The above tables are containing the individual and average value of the incoming TRAFFO and outgoing feeder in DILLA city. The incoming feeder/TRAFFO   that has 132 KV from the grid and the related value is selected according to the data required.

Figure 3.5  Fig a) the graphical representation and b) the bar graph representation

the above figure  fig a) that show the active power flow of the city during peak load condition  when we select  the peak load for all feeder  based on the recorded  EEU data  and fig b)  the bar  graph representation   that shows  the indicate  of power flow with respect to specific time.

Figure 3.6graphical representation of VAR fluctuation b) bar graph representation of VAR fluctuation

The above indicates the reactive power variation of grid connected system in the case of peak load condition.during peak load condition large amount of active and reactive power will exist. Reactive power (VARS) is essential to keep the voltage to deliver active power (watts) through the system. Motor loads and other loads require reactive power to transform the flow of electrons into suitable work. When there is not sufficient reactive power, the voltage sags depressed and it is not possible to push the power required by loads through the lines.

Generally the contingency condition including different stage contingency  and each contingency level for intermes of foult. In this case study area severe type of contingency will be developed that included included three phase sysmetrical foult.

Three-phase symmetrical faults are known to be the most severe in a power system due to large fault currents. However, single phase phase to ground faults are more common faults that occurs. If not checked in due time, these faults may grow to symmeterical fault which is uncommon but most severe.

Table3.3 of average recorded value of voltage, current and reactive power during contingency

| Time in Hour | Voltage during fault condition (V) | during fault condition (A) | during contingency MVAR&MW |  |
| --- | --- | --- | --- | --- |
| 2:30-5:40H 03/05/2019 | 185 | 389 | 35 | 44 |
| 7-9:45H 09/07/2019 | 200 | 504 | 54 | 47 |
| 7:45-8:30H 17/08/2019 | 195 | 502 | 55 | 39 |
| 2:45-4:00H 19/10/2019 | 180 | 453 | 41 | 37 |
| 13:38-19:40H 02/04/2020 | 170 | 342 | 39 | 32 |
| 8:20-9:35H 20/06/2020G.C | 201 | 386 | 37 | 41 |
| 10:45-12:37H 27/07/2020 | 175 | 398 | 31 | 33 |

Contingency can be definite as the non-functionality in the power system of a device. There are three levels of problems in case a contingency occurs:

- None- In this case it is possible to balance out the power system without overloading any other element.

- Severe- Damaging of various elements for example, different load ,lines and transformers, due to their overload falls under this category. Including of the balanced and controlled disturbance or foult in the power system

- Critical- When chances of power system collapse are high and swift due to its instability.in the  critical contingency catagori large disturbance and havy types of foult will be mentioned. In case of thise the critical catagori is difficult in the power system opration.

Figure. 3.7V &I  representation  during  contingency conditions

When we study reactive power during contingency condition the overall analysis based on the EEU recorded data of the case study area. Around seven (7) times the fault will be generated due different reson. During the Fault occurrence in a system the flow of current highly rises and the flow of voltage will be declines. the reactive power flow is increase  because of inflation of system current  and when  manage the system  voltage  we can to control  the system disturbance  reactive  power flow  in [27].

In the  GCMG system reactive power management during contingency  condition  is  to carry out  the contingency selection  by  calculating the two  kinds  of performance  indices; Active  Performance  Index  (API)  and  reactive power performance index (RPI) for each out going feeder  line outage.

The real and reactive power variations are mentioned and the contingency current and voltage as well as the frequency disturbance error will be considered and the average contingency schedule will be selected and sampled from the utility excel sheet.

Contingency Analysis actually provides and prioritizes the impacts on an electric power system when problems occur. A contingency is the loss or failure of a small part of the power system.

The contingency condition includes sudden disturbance and unexpected power existence throughout system voltage profile. The Contingency analysis with the use of AC power flow gives the advantage that it provides power flows in terms of MW, MVAR. Using the AC power flow overloads and accurate voltage limit violations can be found. Performance indices (PI) are considered for ranking the severity of a particular contingency. Conventional power flow methods are used in calculating the indices. There are two types of performance index.

- Line flow performance index (PIlf) : This is the index which helps in determining the extent of line over loads and existence of ac power variation

- Reactive power performance index (PIrp) : This is the index which helps in determining  the reactive power flow and  system bus Voltage limit

. Bus voltages are also influenced by the reactive power which is produced by the generating units and Reactive power performance index  provides information regarding severity of abnormal voltage still the reactive power are within the limits or not

Table 3.4of real and reactive power difference before and after system disturbance

| The real and reactive power difference befor and after system disturbance |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| NO | Start bus | End bus | Pri-conti in MW | MVAR | Post-conti in MW | MVAR Varation |
| 1 | 4 | 3 | 4.14 | 2.18 | 2.73 | 2.93 |
| 2 | 12 | 7 | 2.1 | 1.12 | 2 | 1.53 |
| 3 | 12 | 6 | 3.2 | 1.45 | 2.4 | 1.98 |
| 4 | 12 | 13 | 6.42 | 2.8 | 3.5 | 2.9 |
| 5 | 12 | 14 | 2.4 | 2.01 | 2.2 | 2.03 |
| 6 | 14 | 15 | 1.55 | .92 | 1.34 | 0.98 |
| 7 | 16 | 16 | 3.65 | 2.34 | 3.3 | 2.77 |
| 8 | 15 | 17 | 6.02 | 3.21 | 4.03 | 2.9 |
| 9 | 18 | 18 | 2.7 | 1.54 | 2.2 | 2.01 |
| 10 | 19 | 19 | 4.7 | 2.31 | 3.2 | 2.43 |
| 11 | 10 | 20 | 5.1 | 3.93 | 4.32 | 3.43 |
| 12 | 10 | 20 | 5.3 | 2.9 | 5 | 2.97 |

The above table show bus to bus connection real and reactive power variation before and after contingency. The sampled data are collected from the SNNP electric utility office and the selected and average result of the real and reactive power variation limit is based on the given data short term estimation process.

Figure 3.8 graph representation of reactive power variation before contingency

The reactive power variation before the contingency condition  will be same as small when I comper the reactive power existe during contingency condition   and the graph show the VAR variation  and flow of the reactive power.

Figure 3.8 reactive power fluctuation during contingency condition

The above figure indicates the fluctuation of reactive power during system disturbance or contingency condition ,most of a time same disturbance will be happened the reactive power will be  highly rise and at the same time real power will be  reduce and power factor of system is  low  this indicates to that the grid connected  system has the problem of load disturbance and reactive power management.

.

## 3.4 Frequency control

A novel control strategy which can be applied to MG in both the modes is introduced. This scheme of control allows a DG to control its real & reactive power components in grid-connected mode and to control the voltage & frequency in autonomous mode.

It gives the variations of frequency with respect to time for a given step change in load demand. By considering the first order approximation and the system is assumed to be under free governor operation.

∆Fs∆PcS=0=-PpTt[sS2+R+KpR+Tp]*∆PD

The change of load frequency variation with respect to time will be

∆ft=-RKPR+KP1-e[-t/Tp[RR+Kp+∆t*∆Pd

=   ∆f(t)var=f∆t-∆fdistu*t

=∆fvar=(∆fdisttime*60/(±5%)%∆fnormal)

=50-4.551*60/∆%f(47.5)0.22

=57.41sec

∆(57.41-50)distu=7.41sec

vardist*1*7.41-2.5SSFE%±5=4.91sec

L∆fdisturbance=4.91sec

The system load frequency  disturbance in the different loading condition will be 4.91per sec with out the acceptable limit  or the total disturbance of the steady state load frequency   disturbance  will be  7.41 per second so the existeing system  frequency disturbance will be 4.91/sec.

When the Micro grid  is connected to the upstream network, inverters of the renewable energy sources operate in the PQ control mode, and the voltage magnitude and frequency references are determined, assuming the upstream network as an infinite bus.  However, as soon as the MG disconnects from the upstream network, the VSI inverter provides new references for voltage magnitude and frequency in [30]

Figure 3.10 block diagram of proposed frequency controller loop

The LFC system will be   represented in the fig 10 it has  different  component that are  input side component  integral controller   signal filter  and steady state result displayer. In the input side the disturbed ferequency  will be recived and  to cheek the variation  of disturbance  the  IC will be  control and manage the disturbed signal and sent to  signal chheker  the signal cheeker are  to cheek the rate of the steady stste error and displaye the result.when we control the disturbed  frequency the  error will be more than the accepted rage   the re filter loop will be  sent the signal to IC for re controlling and managing process.

A frequency cutter de-loading control strategy based on the partition control idea for the grid connected AC micro grid containing high-power junk and disturbance system. It can support the frequency stability in the system, and it will not cause the system large impact, which affects the power quality of the system.

At the same time, the priority of distributed power and load is considered in the frequency control strategy, which can realize more economical dispatching and generation tasks, protect the use of important loads, and complete system power distribution and balance in [31]  
The frequency control strategy proposed in this paper aims to provide high quality power supply for the grid connected micro grid and distributed load point  mountainous areas, small islands and other areas that cannot be covered by traditional large power grid.

In addition, as an important part of the frequency control of the grid connected and islanded micro grid, the service life of the battery is related to the economic benefits of the islanded micro grid in [32]

The limitation and dis advantage of the junk method or system are it can’t resist the large load area or not to control easily the steady state frequency error of the system not very fast, accurate and   modernized method to solve and reduce the steady state frequency error . In case of this the integral load frequency control method will be important and acceptable.in [33]

### 3.4.1Automatic load Frequency control

Frequency governor is a process to maintain stability in the power system. In power systems, when the load is more than the supplying power, the frequency in the system will drop. ... Automatic Load Frequency Control (ALFC) is the best approach to control the frequency around the load during different condition  in [34]. including self-system integral load frequency controller (SSILFC).

The two main objective of Load Frequency Control (LFC) are
1. To maintain the real frequency and the desired power output.
2. To control the frequency   change in the PCC power between governed areas  [35]

### 3.4.3 Designing   and Mathematical formulation of   SSLFC( frequency controlling)

Figure 3.11 load frequency controller

Kg = constant of the micro grid governor

Ks =constant of system control

Kp = constant of frequency generation cheekier component

Kp=1/D……………………………………………………..  3.46

Ks=2*HfD……………………………………………………..3.47

Ki=14Kp*Ks*1+KpR………………………………………….  3.48

Ki = 0.312

The change of frequency ∆f in the steady state is the change of load frequency expectations L with result of maximum regulation change β or frequency response characteristics.

∆f =-Lβ

The area frequency response characteristics β

β=D+1    R   …………………………………………………………    3.49

=0.51

D=dPd/df   AND   R is the regulation

D=20%system expected  disterbance the material divation  arc

=0.01 pu

The maximum regulation is 5%= 0.05 or based on line of micro grid specification document

Controlled frequency will be   f new that is

fnew =fold+ ∆f

Total disturbance of load frequency in the system will be 273.33

Disturbance of frequency per second (DFS)

DFS=TDF60sec=4.915

= 4.915 Hz

DLFC=5%*DFS=0.22

=0.22 Hz

Disturbance of Load Frequency Control (DLFC) of the new system will be the product of disturbance frequency system per second with normal version of frequency in the system. fold  means the nominal  or  decaled  frequency  is 50 Hz  but   without  controller  the frequency  is not reach  and approximate  to  the nominal value ..

In an electric power system, Load Frequency Control (LFC) is a system to maintain reasonably uniform frequency, to divide the load between the generators and to control the tie-line interchange plans. Load Frequency management badly needed for power system because if the standard frequency is 50 Hertz and the system frequency vary both said 5%.in[36].

Steps of  Micro grid  system designing and studing

When we model or design the micro grid we must understand and know different tasks. Those are

- Filed study for the case study area (temperature, radiation, wind speed and.…)

- Identification of the micro grid components

- Selecting  the cost effective element of the MG source

- Decide the way of mode operation (islanded mod  and connected )

- Identify the  source component types (renewable ,nonrenewable and mixed )

- The size of designed system

- Governmental declaration and social contraction

The micro grid ( PV, battery invertor , controller  and etc…) include the renewable source grid connected large power generation. When we designed the MG try to include all principle that is mentioned in the above.

## 3.5 Modeling and sizing of PV System

Solar System sizing is the process of evaluating the adequate voltage and current ratings for each component of the photovoltaic system to meet the electric demand at the facility and at the same time calculating the total price of the entire system from the design phase to the fully functional system. As a first step, the electrical devices available at the residence itemized with their power ratings and time of operation during the day to obtain the average energy demand in Watt-hour per day. The monthly average solar radiation data of DILLA city is given in below.

Table3.5 Average temperature and solar radiation data for DILLA from SNNPR energy management office and NASA

| Month | Jan | Feb | May | Apr | Mar | June | July | Aug | Sep | Oct | Nov |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Temperature/c | 34.3c | 33.54 | 35.2 | 29.74 | 29.4 | 32.21 | 31.76 | 33.3 | 29.6 | 35.5 | 33.7 |
| Solar radiation in kwh/m2/day | 6.9 | 6.54 | 6.19 | 6.05 | 5.85 | 5.33 | 6.85 | 3.94 | 5.76 | 5.97 | 4.79 |

In  the micro grid  PV  system designing  we have different  photovoltaic  (PV) energy geaneration  component that  are  PV araye,different  converter ,inverter  and controller . the degining of PV system  are connected  with grid system  in the point of  comment coupling(PCC).the average  temepreatur  and  solar radiation  will be   recorded  the designing  craiteria will be follow the  standared  rule.

Fig 3.12 block diagram of grid connected PV system configuration

### 3.5.1 Sizing the solar array

The daily energy requirement from the solar panel is based on minimum monthly average solar radiation for the design because this is the worst radiation of the month, which is 5.34kwh/day. The system design 48V system and two different 6MW distributed generation with average of selected 3hour  near the optimal location the city distribution system outgoing feeder. The design assumes the DG to operate 4hr per day in the peak load time. The total daily energy demand becomes 8 Mwah.

Er  =energy required  = daily average energy consumptionproduct of component efficiency                                 3.5

9.75MWh

To obtain the peak power of the PV:

Pv = daily energy requirement from panelminimum monthly average solar radation                                                    3.6

1.82MW

The total current needed can be calculated by:

Idc = peak power of the PV        system DC voltage*opreating hour                                                                 3.7

1763.88Amp

Select PV Module Type

Optimum or peak amps of solar module used. See module specifications.

Chosen PV module:

Model Topsun TS-S420TA1

Max Power =802.0526W

Max Current = 11.62Amps

Max Voltage = 48.73V

Nominal Output Voltage 48 Volt

Now the number of module to be connected in series and parallel will be calculated to meet the desired voltage and current.the total dereted of module 0.2mm

First, the number of parallel modules:

Np = whole module currentrated current of one module* Module Derate Factor                                           3.8

Np=Idr  /Ir*Mf =747

Second the number of series module which equals to:

Ns = system DC voltagemodule rated voltage                                                                                   3.9

1

Finally, the total number of module Nm equals the series module multiplied by the parallel module:

Tnm =Ns*Np                                                                                      3.10

=747

Therefore the system have 747 panel connected in parallel.

### 3.5.2 Sizing of the Battery

The amount of rough energy storage required is equal to the multiplication of the total power demand and the number of autonomy days. The total average energy required is 1.82 Mwah and assuming number of autonomy day to be three hour. The total power production will be MW

Es=total power per day*duration                                               3.11

= 5.46MW

Reserve time have taken is1.5 days and batteries are not 100% efficient assuming 80% efficiency. For safety, the result obtained is divided by the maximum allowable level of discharge:

Esafe = energy storage requiredmaximum depth of discharge                                                                    3.12

= 6.82MWh

The capacity of the battery bank needed can be calculated:

C = safe energy storageDC voltage of single battery                                                                            3.13

=142187.5Ah

The total number of battery is determined by:

Lead acid batteries with model of S1900

Rated Capacity = 1400Ah

Battery voltage=12V

This is the total number of batteries in parallel required (Divide line 4 by line 5).

Number of Batteries in Parallel =Required Battery CapacityCapacity of selected Battery                            3.14

=142187.5Ah1400Ah=102 batteries

≈102 batteries

To determine the number of batteries required in series, divide the system voltage (48V) by the voltage of the chosen battery (12V).

Number of Batteries in Series =Nominal System VoltageNominal Battery Voltage                                 3.15

48V12V=4

Total number of the chosen battery needed for the system (Multiply line 2 by line 3)

Total number of the chosen battery needed=Batteries in parallel*Batteries in series

=102*4=408Batteries

### 3.5.3 Sizing of the charge Controller(MPPT)

There are two types of charge controller these are: MPPT charge controller and PWM charge controller .But PWM charge controllers are cheaper than MPPT but create large power losses; up to 60% of power can be lost. This is because PWM do not optimize the voltage going to the batteries; this limitation makes the PWM controller is a poor choices for large system. But MPPT charge controllers optimize the voltage coming from solar panels so that the maximum amount of energy is transferred to the battery. MPPT controllers are 93-97% efficient in converting power. The power output required per house hold (residential), commercial and institution if all appliances are functional at the same time is 1903.645kw and the voltage required for the solar home system which is greater than 4kwh is usually 48V.  So the charge controller must work at a maximum current of IT. Since the system is rated at 48v then the charge controller is also 48v and  the power generated from solar panels are 704.35kw.

Current rating (IT) = power output of pannelsvoltage                                               3.17

IT= 704.35kw48v=14,673.93A

Then multiply the current rating by a safety factor (1.25-1.3) gives14,673.93A*1.25=18,342.41A

Therefore, the MPPT charge controller of 48v and the minimum current rating of 9,342.41A is chosen. MPPT charge controller enables up to 30% more energy yields than PWM charge controller.the current of short circuit of the module is 9.12.

Charge controller current=no. of module*Isc of module*safety factor

Charge controller current=236*9.12*1.25=2690.8A

Therefore 60A charge controller is selected.

Number of Charge controller=2690.8A /30=89.89=90

Arrays controlled by charge controller=9342.41A /90*1.25=83

### 4.1.4 Inverter Sizing and Rating

The sizing of inverter is basically dependent up on the total demand of the system. There are three types of inverter from these inverters more preferable one should be selected. These are:

- Square wave inverters: This is the cheapest type but not suitable for all appliances

- Modified sine wave: The output is also not suitable for certain appliances like fridge and microwave oven.

- Pure sine wave: This is preferable for this thisis work.

The power rating of inverter should be equal or more than the total load in watt at any instant. By taking some margin choose an inverter having 48v DC to 400v/50Hz and minimum power rating of f 1603.645kwAC pure sine wave inverter. For standalone systems, the inverter must be large enough to handle the total amount of watts that will be using at one time the inverter size should be 25-30% bigger than the total watts (w) of appliances. In this case the maximum load at any instant is equal to 1603.645kw

selected panel rated power*safty factor                             3.18

Size of inverter= 704.348kw*1.3=915.65kw

Size of inverter≈916kw

Fig 3.13Circuit diagram of grid connected  PV system configuration

## 3.7 Mathematical formulation of SVC

SVC regulates the voltage by controlling the amount of reactive power absorbed from or injected into the power system.

An SVC can assure perfect voltage stabilization and perfect reactive power compensation at the same time. The requirement for highest power quality precedes the need for perfect reactive power compensation. For optimum voltage stabilization, the variable reactive power output of the SVC hence needs to compensate not only the reactive power of the load, but also correct the voltage variations in [28]

QSVC=  Qload+nP2 2*Ssc+KPload                                                                3.19

With   K=R/X  (the resistance reactance  ratio of impedance )

Where   Qload and Pload are the reactive and active power of load respectively and Ssc is short circuit power

Instantaneous power in a lagging system can be represented by

P=Vmax*Imax coswtcoswt-ϴ

P=Vmax+Vmax*Imax2Cos1+cos2wt+Vmax*Imaxsin ϴsin2wt2     3.20

SVC reactive power generation limit is constrained by the physical range of
the firing angle. It is considered that the angle is allowed to be set between a
maximum and a minimum value.

αsvc min≤αsvc≤αsvcmax                                                                      3.21

The main function of a SVC is to absorb or supply reactive power based on the changing VAR requirement of the load. The current is controlled by the firing angle, which at zero degree the switch is permanently closed, then slowly limits current as firing angle increases to 180 degree where current is then zero. Limiting the current ultimately limits the reactive current which results in how much reactive power can be added to or subtracted from the system.

### 3.7.1Thyristor control reactor (TCR-FC)

A basic TCR includes an anti-parallel connected pair of thyristor valves, 𝑇1 and𝑇2, in series with a linear air-core reactor, shown in the blow Figure. The anti-parallel thyristor pair performances like a bidirectional switch, per thyristor valve 𝑇1 conducting in positive half-cycles and the second thyristor (𝑇2) conducting in negative half-cycles of the supply voltage.

Figure 3.14: TCR-FC Equivalent circuit and Circuit diagram of TCR

The opration of the  The circuit of TCR system is  The thyristor-controlled reactor consists of a reactor in series with two parallel inverse thyristors. The two inverse parallel thyristors are gated symmetrically. They control the time for which the reactor conducts and thus control the fundamental component of the curren and the full opration of the system is depend on positive gate signal and the wave reprseantation  of the opration in the positive get signal will be below.

Fig 3.15 graphical representation of opration of  TCR-FC in the firing angle subject

The basic operation of single phase as well as three phase TCR can be as follows. The source voltage as

𝑉𝑠 (𝑡)=𝑉𝑠𝑖𝑛 𝜔𝑡

From the basic Kirchhoff’s voltage equation

Ldidt-vs=0                                                          (3.22)

Where V is peak value of the applied voltage, 𝜔 is the angular frequency of the supply voltage and L is inductance of the TCR, then the line current can be written as

(t)=1/L ∫Vs(t)dt +C                                                          (3.23)

(t)=-V/ωL cosωt +C

For the boundary condition is (𝜔𝑡=𝛼)= 0

(t)=-V/ωL (cosα- cosωt)

Where α is the firing angle measured from positive going zero crossing of the applied voltage.

The Fourier analysis of equation can be written as

(α)=a1 cosωt +b1 sinωt                          (3.24)

Where 𝑏1=0, because of odd symmetry i.e, f(x) = f (-x). Also not even harmonics are generated because of half wave symmetry i.e, (𝑥+𝑇/2 ) =−𝑓(𝑥)

The coefficient 𝑎1 is given by

a1=4/T ∫(x) Cos (2πx/T) dx

Solving,

A=I1(α)=V/ωL(1-2α/π-1/πsin2α)                  (3.25)

Equation 3.45 can be written as

I1α =V*BTCR(α)

(α)=(1-2α/π-1/πsin2α)

Where 𝐵𝑚𝑎𝑥=1/𝜔𝐿

The TCR is act like a variable susceptance. Variation of firing angle changes the susceptance and consequently the fundamental-current component which leads to a variation of reactive power absorbed by the reactor because the applied ac voltage is constant.

### 3.7.2OPERATING PRINCIPLE OF  TCR-FC based SVC

A thyristor-controlled reactor (TCR) is a reactance connected in series with a bidirectional thyristor valve. The thyristor valve is phase controlled, which allows the value of delivered reactive power to be adjusted to meet varying system conditions. Thyristor-controlled reactors can be used for limiting voltage rises on lightly loaded system. The current in the TCR is varied from maximum to almost zero by varying the firing delay angle. Shunt connected to the line in order to inject variable current. As long as the current injected is in phase quadrature with the line voltage, the shunt Controllers only supplies or consumes variable reactive power.

Simultaneous application of gate pulses a thyristor valve can be brought into conduction .and the valve get automatically blocked the valve immediately after the ac current crosses zero, unless there is reapplication of gate signal through firing angle control method. The current in the reactor can be controlled from maximum (thyristor valve closed) to zero (thyristor valve open).

Valves of thyristor connected in series with the reactor and Circulating current through the reactor (Ir) is controlled. Capacitor supplies the Leading VARs to the system. Rating of TCR is generally higher than the capacitor for supplying lagging VARs to the system in[29]

## 3.8 Neural network

ANNs improves and checked the performance corresponding to the different parameters provided by environmental sensors, if needed it changes the line parameters within the specified range to achieve the desired performance of the line.

Since the processing speed is directly proportional to the number of neurons, therefore, to improve the performance up to the desired level, a number of hidden layers and a number of neurons in each layer can be varied. To acquire desired output, networks take different activation functions between input and hidden layer and hidden and output layer. Similarly, different neurons can also be taken for different layers

The theory of ANN is inspired by the animal brain neuron structure and its ability to deal with huge information. Artificial Neural Network is one of the artificial representations of the human brain that always tries to simulate the learning process in the human brain. There are several Artificial Neural Network Algorithms that are often used for different among others: Back propagation Algorithm, Conjugate Gradient Fletcher-Reeves (CGFR) And Resilient.Artificial Neural Network (ANN) is a computational model, which is based on Biological Neural Network. Artificial Neural Network is often called as Neural Network (NN) Back propagation (BP) algorithm was used to develop the ANN model The typical topology of BPANN (Back propagation Artificial Neural Network). When we apply the ANN controller in the SVC divice .ANN is used to  control and varing the fring angle of the SVC  in order to achive smooth ,better and adaptive control of the reactive power in the GCMG system. In figure 18 show that ANN working flow in the reactive power compensation and disturbed load frequency controlling mechanisim. After initialization of the input and declaration of stage of epoch and hidden layer arrangement the  the ANN signal cheeker will be to cheek and dicide the stage ,itration  and performance  then the controlling signal pakage of the ANN to control the SVC fringe anle and gate signal then the SVC to perform the compensation process as well at the same time the ANN control signal to cheek and control the integral load frequency controller with  net, acuret and with few itration satge  finally the ANN  will be design and displaye each the  toll box,performance indicator, Validation indication and gradient indicator.

Figure 3.16. Flow chart of operation of ANN

Artificial neurons are similar to their biological counterparts. It has input connections which are summed together to determine the strength of their output, which is the result of the sum being fed into an activation function. Though many activation functions exist, the most common is the sigmoid activation function, which produces a number between 0 (for low input values) and 1 (for high input values). The resultant of this function is then passed as the input to other neurons through more connections, each of which are weighted these weights determine the behavior of the network Typical artificial neural network consists of three layers.

- input layer,

- hidden layer and

- Output layer.

Fig3.16 ANN Architecture including different layer

Input layer where the data are introduce to the network and send to ANN data reciver layer.   Hidden layer where the data are processed  to select and control the the accuret  combination.  Output layer where the result  of given input and processed the combination of hidden layer network and to display the controlled and specified output.

The potential of Artificial Neural networks for nonlinear adaptive filtering and management, their ability to predict solutions from the past trends, their huge processing capability, and their ability to produce a quick response in mapping information makes them a really promising tool for their application to power systems the primary work towards the facility system security analysis by pattern recognition technology has been rumored  the unreal Neural Network has been used for varied installation applications like load statement

Artificial neural networks (ANNs) have the potential advantage over conventional techniques in significantly improving the performance of the other techniques. The artificial neural networks (ANNs) have been recognized as useful tools for the identification and control of the system with different nonlinearities. This is so by virtue of the fact that ANNs have the capability of non-linear mapping, parallel processing and learning; these attributes make them ideally suited for power system control application. In the power systems (ANNs) have been successfully used for short term load forecasting, power system control, reactive power compensation, fault detection, harmonic propagation, and so on. The block diagram of the new back propagation neural network (BPNN) system for reactive power compensation and optimization is shown in blow Fig. The method is based on using linear programming technique to generate different training patterns and obtain the input data to ANN. In this respect, the ANN is trained to determine the proper adjustment of the control variables required to alleviate over-voltages, under-voltages and generator reactive power limit violations

Figer.3.18 block diagram  of the BPNN system for reactive power compenseation

The BPNN system consists of four fundamental components which are: Sensitivity Factor Module (SFM), Actual Topology Evaluation Module (ATEM), Linear Programming Module (LPM), and Back propagation  (BP).

This BPNN system is used to adjest the wight and basis of  the network  to minimize  the mean squer error  of the  artificial neural network  and give reasonable answer  to the final  controller and result displayer of the system.

## 3.9 Problem Formulation

### 3.9.1 objective   function and constrint   condtions

The objective and constraint  function  of the system reactive power compensation will be

- Objective function

PD=PDO+1+λ.                                                                          (3.26

QD=QDO+1+λ                                                                         (3.27

PDO and QDO   correspond to original load or base case and λ load ability parameter of the load

- Constraints.

Basic equality constraints correspond to the power flow equations in every load

∆Pi=Pgi-Pdi-Pi                                                                   (3. 28

∆Qi=Qgi-Qdi-Qi                                                                (3.29

Where Pgi and Qgi and real and reactive power of the generator; Pdi and Qdi the real and reactive power of the load and Qi and Pi is the power injected of the system

The load Voltage in the final load reading position

Ui =Ui<θi

Power consumed by loads connected system

Loads are characterized by a static exponential model, considering a power constant model

(  = β  = 0), in which active and reactive power consumed by the load is expressed as:

PDi =PDOU/Uopα

QDi=QDoU/UoQβ

Where Uo, PDO and QDO are the reference voltage, active and reactive power of the system

Reactive power injected by the SVC in load terminal will be

QSVCαSVC=U2XC -U2BSVCαSVC

Inequality constraints constitute the physical limits of the components or operational constraints in the system. The maximum power injected by micro grid system is constrained by the maximum capability of each wind turbine and PV system. At the same time the reactive power limit and injection and observation will be presented Active power injected by the Active power output is restricted by lower and upper limits:

Pl min≤Pli≤Pl max                                                                      3. 30

Ql min≤Qli≤Ql max                                                                     3. 31

Where Plimin and Plimax are the minimum and maximum operating power. The capability constraints are related to the Reactive Power capability

### 3.8 .2)Minimize Var Cost and Real Power Losses

Model1    =      minCQ +CPloss                                     . 3.32

=VARn=k=0nC0+Ck*Q+aCn-k*Qn

Fmincost =C1(Q)c+k=0nnkC2(Ploss)

Ploss= m=1ngm(V1m  +2 V2m2)-2V1m2Vmcosθ

Model2  =  minCo+C1Qc*X+C2Ploos               .3.33

The boundary of reactive power and loss that are expect and exist in the system will be

Ploss max>Ploss   and Ploss    >Ploss min

Pl0ss min≤Ploss≤Ploss max                                                      3.34

Under integrated grid arrangement the compensated reactive power constraint or boundary will be

Qexp >  Qmax       and  Qexp ≤  Qmin

Ql0ss min≤Qloss≤Qloss max                                    3.35

# CHAPTER -4

# 4.  RESULT AND DISCUSSION

## 4.1 Result

ETAP is the most comprehensive analysis boards for the design, simulation, operation, and mechanization of generation, distribution, and industrial power systems. ETAP is advanced under recognized quality declaration program and is used worldwide as a high impression software. ETAP is totally localized in four languages with interpreted output reports in six languages. As a fully unified initiative solution, ETAP extends to a Real-Time Intelligent Power Supervision System to monitor, control, automate, simulate, and optimize the operation of power systems Different power distribution system simulation for consistency analysis is done using ETAP software. In ETAP the Distribution System Reliability Analysis employs a new analytical algorithm to assess the consistency indices of mixed radial and meshed distribution systems. This algorithm essentially uses the algorithm for radial distribution systems since the meshed network, if any, is first transformed to a radial network. Therefore, the employed algorithm is fairly effective and suitable for large-scale distribution systems of general configurations. This simulation result shows basic reliability indicator at each of section of the models. And show brifly the real and reactive power flow with resepect to system real power loss.

When we came to the Grid Connected Micro Grid system we have 132/33/15KV distribution feeder transformer in the grid-connected system and from the grid-connected line five large outgoing line will be existed that is DILLA line1, DILLA line 2, GOLOLCHA line, YERGACHEFFE line, and  SOLOMO power line are the grid-connected TRAFFO   and each out ging feeder or traffo are instolled frome different rated output transformer(15 KV&33KV) in addition to that we have four sub feeder in side the 15KV feeder side.  I will try to analyze and study only DILLA  city and all feeder are arranged and installed from the 15 KV feeder line total In the DILLA city we have four  different rated distribution sub feeder system and each feeder have different power flow rate.

.

Figure4.1 normal  grid connected micro grid load flow and feeder arrangement by ETAP

In the micro grid side we have mini micro grid sources component  that are PV.  PV panel that is used to collect and absorbed solar energy then the DC-DC converter converts the produced dc voltage to the required quality and limit of dc power then connect to the DC bus by using bi-directional inverter converts the produced DC power to AC then install to ac bus finally the produced power flows through ac system to grid.  large amount of real and reactive power will be developed because of the controlling device will be the manual series capacitor bank system. The general system load flow, the real and reactive power flow and loss will be presented in appendix –C.

## 4.2 Grid connected system during peak load condition

Figure 4Simulink diagram for grid connected micro grid system during peak load

The grid-connected micro grid systems are the combination or integration of different renewable energy generation systems with the national grid line. The designed Micro grid system includes PV system. On the grid side, the controlling and compensation device will be a manual capacitor bank system and it has a large amount of real and reactive power loss . Totally we have around 40.56MW and 27.0816 MVAR amount of power is flow. At the point of PCC disturbance will be developed because of load unbalance and frequency deviations as well as a large amount of reactive power flow. In case of this, reactive power management and frequency control mechanisms will be required for the reactive power management, rated flow of power, and reduction of steady-state frequency error at the common coupling terminal and system  load .

Figure 4.3 graphical representation of active and reactive power of GCMGS

The above Simulink scope  diagram expressed the flow of active and reactive power flow in the general system of grid-connected micro grid system without controlling of SVC device or by manual/old capacitor bank and the red and black color are indicate the real power and reactive power flow throughout the system respectively and additionally we can express a large amount of reactive power flow will be presented in because of the existing controlling device.

Figure 4.4Simulink graph of Active power for peak load condition

Above fig. 4.4 show the flow of active  power  through the system during peak load condition during this time  the micro grid is  send large amount of energy to the grid in case of this large amount of real power  will be flow when we compear to the normal condition power flow.

## 4.3GRID CONNECTED MICRO GRID SYSTEM DURING CONTINGENCY

Figure 4.5Simulink of   GCMG system during contingency condition

During contingency condition the real and reactive power flow through will be fluctuated  when we compare the peak load condition.  the current that are flow the system will be increase  and the  average voltage at the load and PCC terminal will be disturbed.and the power flow during contingency condition (three phase sysmetrical foult )36.89MW and 30.34MVAR  active and reactive power  will be flowed respectively.

Figure 4.6of Simulink result of active and reactive power flow of GCMG during contingency condition

Figure 5of Simulink result of voltage disturbance during contingency condition

During the contingency condition the reactive power will be increase highly  as well as fluctuated and the active power existed in the system will be reduced parallel because during contingency condition  the system voltage is  disturbed and the current passing thought the GCMG power line  are rise.  So current during system  disturbance is increase and large amount of reactive power produced.  The current that exist in the GCMG system during contingency condition will be increase up to the disturbance is maintain.

Figure 4.8 Voltage and current disturbance during contingency condition

During contingency condition the voltage and current will highly disturbed the current inflation will be high during disturbed and at the same time the voltage flow in the system will be decline.

## 4.3 STATIC VAR COMPENSETOR (SVC) with TCR-FC

The TCR is act like a variable susceptance. Variation of firing angle changes the susceptance and consequently the fundamental-current component which leads to a variation of reactive power absorbed by the reactor because the applied ac voltage is constant.

Figure 4.9of Simulink diagram for of thyristor control reactor with fixed capacitor of SVC

## 4.4 LOAD FREQUENCY CONTROLLE

When  we study and control  the frequency  the main  and important  thing  will be to  control and reduce the change / variation of  frequency  in the PCC  load area  from the disturbed  nominal frequency.

Ki=14Kp*Ks*(1+Kp/R)2

Ki = 0.212

The controller is the most important in the system frequency controlling and steady state   error minimization.

Figure 4.10of Simulink diagram of load frequency controller with integral controller

Frequency variation go to nearest point of zero when we use load frequency integral controller   in the grid frequency controller this integral controller used to reduce the steady state frequency error and dynamic disturbance error GCMG system operation.

inperoved percent=n=1∞(DFS-DFLC)/DFS

FI=n=1∞4.55-0.224.55*100= 96%

The steady state frequency error in the Point of Common Coupling (PCC) and load are reduced and the system frequency will be improved.

General the steady state error declination and improved frequency performance graph will be presented in APPENDIX-II .The function of ILFC (integral load frequency controller) completely control the steady state frequency variation and error within fraction of second.  By single programming order of ANN. The ANN are used to control the  integral Ki and Kp component  the  controlling process  and the load frequency controller to control the frequency disturbance  properly and acuretly  deu to ANNcontrolthe ILFC in the load terminal.

## 4.5 Grid connected micro grid system with controlling system

Figure4.12 Simulink of GCMG system reactive power compensation by ANN of SVC and LFC system .

For simulation, the three phase AC voltage source is of 132KV, 50 Hz is taken. Different power feeders for different power flow rate is taken in the grid connected micro grid system the real power and reactive power in the load is measured using the Active & Reactive Power measurement Block. By different firing angle and  Load Characteristics has been studied. In the grid connected micro grid system large amount of reactive power, load disturbance and real power loss is existed. For the controlling and compensation process the SVC component is very important for the above mentioned problem. The General GCMG Simulink structure have different sub system one of them are SVC COPM. It is used to reactive power managing process and real power improvement. But in addition to the SVC we have ANN of SVC it ordered by single program that are used to reduction and compensation of the system reactive power, indication of percent of improvements for each general feeder controlling point and identification of the system reactive power for each feeder and to control the SVC compensation process for accurate operation result of the system. the general ILFC system are used to reduce and correct the steady state frequency error of the load system. And the feeder continuity controller is used to control and maintain the continuity of the each sub feeder and load during different conditions.

Figure 4.13Simulink of active and reactive power after compensation process

The above fig.4.13 show the flow active and reactive power  existence During ANN based SVC controlling and compensation process the active power will be improved and the reactive power will be compensated properly.

Figure 4.14Simulink result of Active and reactive power after compensation

Figure 4.15reactive power flow of  artificial neural network controlled SVC

Figure 6active power flow of the based on artificial neural network controlled SVC

In the figure 33) Simulink result of active and reactive power after compensation when we use SVC for the compensation process the real and reactive power flow will be improved 40.56MW to 50MW and the reactive power is compensated to 17.34 MVAR and the voltage and current flow of the GCMG system after applaying  SVC the disturbance of voltage and inflation of current will be maintain or controlled. The system at the same time to controls the current and voltage flow, the load side frequency disturbance and steady state frequency error will be reduced and controlled by using an integral load frequency controller. In the fig 4.14 shows that the three phase reactive and active power flow of the GCMG system. fig 4.15 indicate the reactive power flow of the three individual line of the system around load and PCC based on ANN of SVC and fig 17 show the active power flow individual line of the GCMG system in the process of reactive power compensation process of the ANN control of SVC and the real power will be improve. The improved power in each feeder will be represented in the blow figure.

Figure 4.17  of graphical representation of improved active power of the GCMG system in variable load

The improved power of each feeder during variable load will be different that means the power improved during contingency, peak load and normal power flow are different power flow rate. The ANN system neural network tanning, validation and performance will be presented in the APPENDIX -II

In the existing system when we substitute the static VAR compensator (SVC) in the place of the capacitor bank (CB) the reactive power and loss of the system will be reduced. The SVC is more important than capacitor bank CB because the existing system reactive power compensation process is by manual capacitor bank CB system.  In the case of the capacitor bank (CB )  a large amount of reactive power flow and real power loss is developed but when we use static VAR compensator  (SVC) in place of CB the existed reactive power and real power loss reduction. So the static VAR compensator is more reliable and smart for the operation of reactive power compensation and controlling the process.

Table 4.1 comparession analysis of with and without SVC

| comparison of result with and without SVC |  |  |  |
| --- | --- | --- | --- |
|  | Without SVC |  | With SVC |
|  | Peak load | contingency |  |
| Real power | 40.56MW | 36.03 MW | 50.5285MW |
| reactive | 27.08 MVAR | 30.84MVAR | 17.34MVAR |
| Power factor | 83.3.0% | 76.0% | 94.0% |

The expected system disturbance is based on contingency condition power flow rate because in the  contingency condition the GCMG system voltage  and current will be highly disturbed  within fraction  of second  in case of this load frequency and reactive power  will be  disturbed and finally the outcome active  power flow through the system is highly  decline and reduced.

Fig. 4.18 Simulink graphical representation of   maintenance and controlling of steady state frequency error

The ANN are used to control the  integral Ki and Kp component during the controlling process.   the load frequency controller to control the frequency disturbance  properly and acuretly  deu to ANN control the LFC in the load terminal.by single controlling  program of the ANN in the load  frequency  area.

Befor the controlling  process the disturebed frequency range will be 4.92Hz and the  after controlling process the steady state frequency error will be 0.22Hz.

The disturbance of the system depends on the general power flow rate and the feeder flow rate or load capacity. When we apply artificial disturbance in the general GCMGsystem the system load frequency  will be highly disturbed and the ..  The total power of the max load condition will be 41.504MW and the contingency condition power will be 36.803MW.

When we compare the compensation process with the different controllers to present  a different result. in the previous and the first controlling technic, that is ANN controlled SVC the reactive power will be highly compensated 17.34MVAR and applying of  the fuzzy system in the general system the reactive power will be compensated around 18.23MVAR result will be recorded and  finally when I use the MOFAinthe GCMG system  reactive power compenseation and controlling process  the the optimal reactive power will be 17.84MVAR. In thegeneral  comparison and finding of the optimal VARvalue. the optimized result between ANN-based SVC , FUZZY based SVC and MOFA system. the ANN will be effective  and more prifereble than the FUZZY and MOFA. And the best and effective controlling algorithm for a finding of optimal result in the compensation and the controlling process is artificial neural network (ANN) more prifereable  and acceptable alegorithim  the the above.

Table4.2 Comparission of ANN,FUZZY and MOFA controller for  finding of optimal MVAR

| Optimal power in the GCMG of both controller in the MOFA |  |  |  |
| --- | --- | --- | --- |
|  | ANN of SVC | FUZZY of SVC | MOFA |
| Reactive power | 17.74MVAR | 18.28MVAR | 17.84MVAR |
| Active power | 50.53MW | 48.463MW | 49..53MW |

In the above comparission table the different algorithem(ANN,MOFA and fuzzy system) will be presented and  to indicate the optimal result of reactive power  in the gride connected micro grid system  for reactive power compensation.

Figur4.18   optimal reactive power indication of ANN and FUZZY system   with MOFA

In the finding of optimal value  of system reactive power   the ANN between FUZZY and MOFA  system .the artificial nural  network  controlling in the SVC  will be well  performed than  the fuzzy system  and MOFA  and  the selected algorithem will be  used to indicat the optimal value of the system. When we see the above  optimized graph .

## 4.6 Power Loss & cost minimization

Before applying   any controlling and compensation process GCMG system total load flow will be 50.56MW and 33.16MVAR of peak load.The loss which is existed before compensation and real power improvement with regards to grid connected and SVC compensation was calculated in the combination of eq 3.12, 3.24, 3.30. We get

Ploss=Psourc-Pload

Before compensation the active and reactive power will be mentioned. the active power loss in all feeder or load category load area will be 3.9MW.according to the first GCMG system by ETAP.	After compensation the improved power will be

P loss =p source – p load

=10.046MW

Previously when we study the system without SVC controller is like existing system of the grid connected system has and installs old controlling and compensating method that are including manual controlling system. This method are not that much important because in the existing system present large amount of real and reactive power loss.

In the privies system the active power loss will be highly generated around 3.95MW per year presented this means in the privies controlling and compensation device will be is not control and compensate properly.

In the normal flow 39.78 MW active powers will be flow with time and after compensation the active and reactive power will be 50.5285MW and 17.34 MVAR. When we see the difference of the reactive power before compensation and after compensation, when we can to re call the reactive power variation formula 3.25 &3.33 we get

∆Q= Qold -Q new

Cheng of reactive power is the difference of the privies system reactive power with the reactive power that are existed after compensation

∆Q = 27.16Mvar -17.43 MVAR

= 10.34Mvar

The real and reactive power at the city load terminal after compensation and controlling process for all feeder will be 50.5284MW and17.34 MVAR. The percent of improved power

%P=Pimproved -PloadnormalPloadnormal*100

%P=∆PPlnormal*100

%P=60.84.0 -39.7839.78*100

= 52.18%

The percent of reactive power improved (compensated)

%Q=Qcomp-QloadQload*100

%Q=∆QQl*100
=33.16-17.8317.83*100

=87.02%

The percent of improved real and reactive power 52.18% and 87.02%respectively and the existing real and reactive power management is not sufficient because the privues  load real and reactive power reading and recording indicates the grid connected micro grid system without SVC controlling and compensation have big difference from the power flow and system disturbance that are existing after compensation.

In the reactive power compensation process the real and reactive power   will be improved and compensated in the grid connected micro grid system without the SVC compensation device will be 40.56MW and 27.16MVAR respectively.

The power factor before compensation process

S=P+jQ

=  40.56+j27.16

Sold = 3674.13    =48.8

The power factor will be

Pf=active power/ Apparent power

=0.837=0.83

The power factor before SVC compensation Pfold is   83%

After compensation the active power and reactive power will be improved and reduce respectively 50.5284MWand 17.34MVAR

The apparent power will be   Snew

S = 4116.2    =53.16

Pf=active power /Apparent

= 50.024/53.16 =0.94

After compensation process the power factor Pfnew   of the grid connected micro grid system will be improved to 94%

Figure 4.19 power factor improvement graph

The fig 39 show the the existence of  power factor  befor  and after  compenseation process .after compenseation  of reactive power the active power flow  will be inprove in case of this thepower factor of the system will be improved.

### 4.6.1Cost analysis of the real power loss in the GCMG system

The annual power loss will be calculated with and without controlling device (SVC). System power loss without SVC is

Anual energylossAEL=PL*8760h

=451.6kw*8760h=3950760kwh

Total power loss in birr CT1=.65*3950760kwh=2567994birr

After reactive power managing process the active power loss will be 101.82kw per day. The annual power loss with SVC is

Anual energylossAEL=PL*8760h

=101.82kw*8760h=891417.6kwh

Total power loss in birr CT2=0.65*891417kwh=579421.1birr

Net power loss of the system in birr

net costcheng=CT1-CT2

=1988572.95  ET. BIRR

Table  4.3    The total annual power loss in birr  with and with out SVC

| Mesurment/unit Of power | Without SVC | With SVC | Difference /saved |
| --- | --- | --- | --- |
| Net in KW | 3950760 KW | 891417KW | 3059343KW |
| Net in MW | 3.95MW | 0.892MW | 3.06MW |
| In ET. birr | 2567994 birr | 579421.1birr | 1988572.95 |

So the total loss power with out ANN-SVC  controlling and compensation process 2567994 birre per year  will be  existed and after applying of ANN-SVC the total power loss of GCMG system  will be  579421.1 birr  per year will be losted.

When  I compenseat the reactive power flowe in the  grid connected micro grid  system  to reduce the large amount of  reactive power flowe and active power loss   by compensation process. During this time the active power flow will be improved  and the var cost is highly reuced.

Cheng of reactive power is the difference of the privies system reactive power(before the compensation and controlling process) and  the reactive power that are existed after compensation

∆Q= Qold -Q new

∆Q = 27.16Mvar -17.43 MVAR

= 10.43Mvar

The total compensated  vare  rate will be 10.43MVAR and the minimized VARcost will be

VARcost=∆Qreducedyear*Billingbirate

Varcost=10430*365d*0.65birr

=2,474,517.5Et. birr

The reduced var cost in the general grid connected  micro grid  system will be 3660767.5 ethiopian birr. That means the annual seved birr deu to reactive power compensation  and load frequency control 10430KVar or 247417.5 ET.birr.

Dilla substations the total energy loss before and after compensation and controlling process in a year:

- Before compensation total power loss = 3950760 KW

- Before compensation  power loss in one year = 451.6kw*8760h

= 3950760kwh KWh

Then after compensation can be saved is: 3059343KW

- After compensation  can be saved in one year =  3059343KWh

- After compensation the reactive power  will be =
Varcost=10430*365d*0.65birr

=2,474,517.5Et. birr

Table 4.4 the investment cost of The MG system for selected material

| No | Name of material | Price in birr | quantity | Total price in ETB |
| --- | --- | --- | --- | --- |
| 1 | PV module | 4155 | 747 | 381,375 |
| 2 | inverter | 1980 | 3 | 5940 |
| 3 | converter | 2500 | 3 | 7500 |
| 4 | battery | 260 | 102 | 26520 |
| 5 | Controller(MPPT) | 4500 | 102 | 459000 |
| 6 | Controller radii | 1450 | 1 | 1450 |
| 7 | Add sour stand | 7260 | 1 | 7260 |
| 8 | Integral cont FCS | 2974.23 | 9 | 26768.07 |
| 9 | Senser BBTI | 11470.39 | 1 | 11470.39 |
| 10 | System controler | 21845.67 | 1 | 21845.67 |
|  | Total birr |  |  | 1,651,511 |

The material investment cost will be 1,651,511 birr is invested during the micro grid is developed

When we calculate the total payback period   to calculate and find the 10%instalation cost and 2%of the maintenance cost. And  total loss of the system  is

2474517+2567994= 5042511ETB

Assuming that the installation cost 10% and annual maintenance cost are 2% in distribution system.

- 10% of 5042511= 504251.1ETB

- 2% of 5042511= 100850 ETB

Total investment cost = 504251.1ETB +100850 ETB ETB+1,651,511ETB

= 2256612ETB

Total back payment =  Total gained power lossTotal Ivestment cost = 5042511ETB2256612ETB = 2.24

Total back payment = 2year in 2 monthly

# Chapter five

# 5. Conclusions and recommendation

## 5.1Conclusions

The three-phase AC voltage source is 132KV, 50 Hz is taken. Different power feeders for the different power flow rate is taken in the grid-connected micro grid system. the real power and reactive power in the load is measured using the Active & Reactive Power measurement Block. By altered firing angle controlling system and mechanism, different Load Features have been studied. The GCMG systems are having problems with reactive power management and frequency disturbance in the system load and PCC. ANN-based SVC and load frequency controller will be proposed for the controlling of the reactive power and frequency disturbance of the system and the feeder continuity controller are used to control the feeder continuity during the different loading condition. Reactive power planning and management provide the strategy of reactive power compensation so that the real power loss can be reduced and the system voltage profile and power factor can be improved. In our country, several Micro grid in off-grid mode, where many of them are shut down due to grid connection challenges of active and reactive power management and with high frequency variation.

The thesis was aimed Reactive Power compenseation and load frequency disturbance  by using ANN-SVC and LFC system in the Grid connected micro grid system (GCMG). The reactive power compensation and load frequency controller are studied with a mathematical modeling. the complete micro grid and national grid path system including different electrical components and the existing grid system have and respond small amount of electric power when we consider the installed capacity. For prevention of power wastage (power loss) and frequency variation in grids connected systems system manager and control will be model or designed by mat lab Simulink. the real and reactive power will be analysis and managed for each moment, the real and reactive power during peak load condition will be 40.56MW, 27.16MVAR, during contingency condition the real and reactive power will be 36.03MW and 30.42MVAR additionally large amount of current flow will be existed or developed and the frequency will be highly disturbed or fluctuated with a fraction of second. but after controlling and compensation the real power improved to 50.5284MW, the reactive power will be compensated to 17.34MVAR this means the real power 52.18% improved, and the reactive power 87.02%compensated, the steady-state load frequency error, and the GCMG system power factor will be improved to 96%and94%respectivly . Without compensation of SVC or existing system is a design by ETAP software and based on the model we get the load flow and real and reactive power loss. the general system and proposed controller are modeled and design by Matlab Simulink package.

5.2Recommendation
    The major issue to be addressed in the grid connected micro grid system for the 132KV line path system should be the issue of power quality problem such as large amount reactive power  consumption and frequency distortion will be developed because of the old manual capacitor  banking system  and unbalance load combination  in the PCC. So, the Ethiopian electric power utility should give attention to overcome this reactive power management declination of steady state frequency error development for the power quality problems and their consequence.

In addition, it should take remedial actions and deal on techniques how to reduce the un wanted reactive power flow voltage disturbance and frequency  distortion in the  grid connected micro grid system  and to compensate big reactive power consumption.

## 5.3 Future work

The proposed AAN based SVC system give better results for GCMG system problems with reactive power management and frequency disturbance. Proposed system with different algorithms can be applied task to another case study area and optimization tecnic  including like energy forecasting, unit commitment, Economic dispatch and maintenance scheduling.

# Reference

[1]	V. M. Awasth and V. A. Huchche, “Reactive power compensation using D-STATCOM,” 2016 Int. Conf. Energy Effic. Technol. Sustain. ICEETS 2016, pp. 583–585, 2016, doi: 10.1109/ICEETS.2016.7583821.

[2]	N. K. Roy, H. R. Pota, and M. J. Hossain, “Reactive power management of distribution networks with wind generation for improving voltage stability,” Renew. Energy, vol. 58, pp. 85–94, 2013, doi: 10.1016/j.renene.2013.02.030.

[3]	A. Jafari Aghbolaghi, N. Mahdavi Tabatabaei, N. S. Boushehri, and F. Hojjati Parast, Reactive Power Control in AC Power Systems. 2017.

[4]	B. N. Farah, “A_simulation_model_for_machine.,” vol. 48, no. June, pp. 214–221, 2019.

[5]	A. Águila Téllez, G. López, I. Isaac, and J. W. González, “Optimal reactive power compensation in electrical distribution systems with distributed resources. Review,” Heliyon, vol. 4, no. 8, 2018, doi: 10.1016/j.heliyon.2018.e00746.

[6]	IEEE researche group  “ Reactive Power Compensation and,” pp. 43–56, 2017.

[7]	S. Aminzadeh, M. Tarafdar Hagh, and H. Seyedi, “Reactive power management for microgrid frequency control,” Int. J. Electr. Power Energy Syst., vol. 120, no. March 2019, p. 105959, 2020, doi: 10.1016/j.ijepes.2020.105959.

[8]	H. Hu, W. Wu, S. Xiao, M. Tan, and C. Han, “Summary on Reactive Power Compensation Technology and Application,” no. Icicci, pp. 225–229, 2015, doi: 10.2991/icicci-15.2015.48.

[9]	F. Ayalew, S. Hussen, and G. K. Pasam, “Reactive Power Compensation: a Review,” Int. J. Eng. Appl. Sci. Technol., vol. 03, no. 11, pp. 1–7, 2019, doi: 10.33564/ijeast.2019.v03i11.001.

[10]	G. Chicco and G. Gross, “Current issues in reactive power management: A critical overview,” IEEE Power Energy Soc. 2008 Gen. Meet. Convers. Deliv. Electr. Energy 21st Century, PES, no. August 2008, 2008, doi: 10.1109/PES.2008.4596731.

[11]	H. Amaris, M. Alonso, and C. A. Ortega, “Reactive Power Management of Power Networks with Wind Generation,” Lect. Notes Energy, vol. 5, 2013, doi: 10.1007/978-1-4471-4667-4.

[12] Hu, Hong Wu, Wenmei Xiao, Shaohua Tan, Min Han, Chuanjia , Reactive Power Compensation  Technology and Application issu Icicci” pp. 1–27, 2015.

[13]	F. Muhammad, “Reactive Power Compensation by Power Capacitor Method,” Eng. Technol.OpenAccessJ.,vol.1, no. 3, pp. 92–95, 2018, doi: 10.19080/etoaj.2018.01.555565.

[14]	L. Liudvinavičius, “The methods of reactive power compensation in the 25 kV, 50 Hz contact network,” Transp.Probl.,vol.13,no.1,pp.59–68,2018,doi: 10.21307/tp.2018.13.1.6.

[15]	E. Rokrok, M. Shafie-khah, and J. P. S. Catalão, “Review of primary voltage and frequency control methods for inverter-based islanded microgrids with distributed generation,” Renew. Sustain. Energy Rev., vol. 82, no. November, pp. 3225–3235, 2018, doi: 10.1016/j.rser.2017.10.022.

[16]	M. S. Mahmoud, S. Azher Hussain, and M. A. Abido, “Modeling and control of microgrid: An overview,” J. Franklin Inst., vol. 351, no. 5, pp. 2822–2859, 2014, doi: 10.1016/j.jfranklin.2014.01.016.

[17]	V. Huchche, “Reactive Power Compensation of the Grid Connected PV System,” Helix, vol. 9, no. 6, pp. 5830–5840, 2019, doi: 10.29042/2019-5836-5840.

[18]	N. K. Roy, H. R. Pota, and M. J. Hossain, “Reactive power management of distribution networks with wind generation for improving voltage stability,” Renew. Energy, vol. 58, no. October, pp. 85–94, 2013, doi: 10.1016/j.renene.2013.02.030.

[19]	S. S. Kanojia and S. Rajyaguru, “Reactive power compensation for LV distribution network,” Int. J. Innov. Technol. Explor. Eng., vol. 8, no. 6, pp. 1734–1741, 2019.

[20]	M. E. Elkhatib, R. El Shatshat, and M. M. A. Salama, “Decentralized reactive power control for advanced distribution automation systems,” IEEE Trans. Smart Grid, vol. 3, no. 3, pp. 1482–1490, 2012, doi: 10.1109/TSG.2012.2197833.

[21]	U. Holmberg, T. Sjögren, and J. Hellström, “Comparing Centralized and Decentralized Banking: A Study of the Risk-Return Profiles of Banks,” pp. 1–33, 2012.

[22]	S. X. Chen, Y. S. F. Eddy, H. B. Gooi, M. Q. Wang, and S. F. Lu, “A centralized reactive power compensation system for LV distribution networks,” IEEE Trans. Power Syst., vol. 30, no. 1, pp. 274–284, 2015, doi: 10.1109/TPWRS.2014.2326520.

[23]	H. BOUDJELLA and F. GHERBI, “Modelling and Simulation of Static Var Compensator (Svc) in Power System Studies By Matlab,” vol. 53, no. 9, pp. 1689–1699, 2013.

[24]	Y. Saratkar and A. Pachori, “Reactive Power Compensation in Transmission Line using Fuzzy Control Method : A Survey,” no. 1, pp. 1–4, 2013.

[25]	G. Sheng, G. Tu, and Y. Luo, “Application of Artificial Intelligence Techniques in Reactive Power/Voltage Control of Power System,” Electron. Sci. Technol. Appl., vol. 1, no. 1, p. 5, 2014, doi: 10.18686/esta.v1i1.2.

[26]	R. Hooshmand and M. Joorabian, “Application of artificial neural networks in controlling voltage and reactive power,” Sci. Iran., vol. 12, no. 1, pp. 99–108, 2005.

[27]	A. Mishra and V. N. K. Gundavarapu, “Contingency management of power system with Interline Power Flow Controller using Real Power Performance Index and Line Stability Index,”AinShamsEng.J., vol. 7, no. 1, pp. 209–222, 2016, doi: 10.1016/j.asej.2015.11.004.

[28]	Y. T. GEBREYES, “Studies on Voltage Control of Distribution Substations Using Static Var Compensators,” no. January, p. 88, 2019.

[29]	J. K. Dash, “Control Strategy for Reactive Power Using Fc-Tcr By Matlab Simulink,” Int. J. Electr. Electron. Eng., vol. 2, no. 4, pp. 39–43, 2015.

[30]	T. Bharath Kumar & M. Uma Vani, “Load Frequency Control in Two Area Power System Using Anfis,” Int. J. Electr. Electron. Eng. Res., vol. 4, no. 1, pp. 85–92, 2014, [Online]. Available:http://www.tjprc.org/view_archives.php?year=2014&jtype=2&id=46&details=archives.

[31]	P. Si, A. P. Hu, S. Malpas, and D. Budgett, “A frequency control method for regulating wireless power to implantable devices,” IEEE Trans. Biomed. Circuits Syst., vol. 2, no. 1, pp. 22–29, 2008, doi: 10.1109/TBCAS.2008.918284.

[32]	Y. Liu, X. Wang, and S. Wang, “Research on frequency control of islanded microgrid with multiple distributed power sources,” Processes, vol. 8, no. 2, 2020, doi: 10.3390/pr8020193.

[33]	N. K. Bahgaat, M. Ibrahim, M. A. Moustafa Hassan, and F. Bendary, “Load frequency control based on modern techniques in two areas power systems,” Adv. Syst. Dyn. Control, no. April, pp. 163–191, 2018, doi: 10.4018/978-1-5225-4077-9.ch006.

[34]	R. Umrao, S. Kumar, M. Mohan, and D. K. Chaturvedi, “Load Frequency Control methodologies for power system,” ICPCES 2012 - 2012 2nd Int. Conf. Power, Control Embed. Syst., no. December, 2012, doi: 10.1109/ICPCES.2012.6508133.

[35]	J. Lee and H. Kim, “Load Frequency Control of Power System using Energy Storage System,” pp. 8–11, 2013.

[36]	D. L. D and D. Z. R, “Load Frequency Control in Deregulated Power System,” Int. J. Res. Arts Sci., vol. 5, no. Special Issue, pp. 124–133, 2019, doi: 10.9756/bp2019.1002/11.

[37] Madhavanunni, A. N. Baby, Jithin Arya, S. S. George, Jisha George, Jobin Renjith Kumar, D.Fuzzy logic controller for reactive power compensation. page 54-59year -2016 issu ,febrewary

[38]. Desai, Dhavalkumar ,Arya, SwapnilReactive Power Compensation Using FACTS Device vol -1,issu jan 2008 page 157- 188 ,year 2018,

[39]. Al-rubaiey, Hasan I Al-rubayi, Rashid H  ,An Artificial Neural Network Based Real-Time Optimal Reactive Power Flow for Improving Operation Efficiency vol -7 issu -3  page 1159-1169 ,year 2017 .

# APPENDIX

APPENDIX – A

2012 E.C SNNPR DILLA CITY DISTRUBUTION FEEDER POWER FLOW

| Bay / Feeder Name |  | Peak Load September 2013 |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Power (MW) |  |  |  | Current (Amp) |  |  |  | Date |  | Time |  |
|  |  |  |  |  |  | R | S | T |  |  |  |  |  |
| TRAF 1 (15 KV) |  | 9.9 |  |  |  | 446 | 446 | 446 |  | 2/13/2012 |  | 20:00 |  |
| TRAF 2 (33 KV) |  | 3.45 |  |  |  | 76 | 76 | 76 |  | 3/13/2012 |  | 20:00 |  |
| LINE 1 (15 KV) |  | 0.17 |  |  |  | 8 | 8 | 8 |  | 22/12/2012 |  | 20:00 |  |
| LINE 2 (15 KV) |  | 1.06 |  |  |  | 48 | 48 | 48 |  | 22/12/2012 |  | 20:00 |  |
| LINE 3 (15 KV) |  | 4.1 |  |  |  | 185 | 185 | 185 |  | 23/12/2012 |  | 18:00 |  |
| LINE 4 (15 KV) |  | 2.6 |  |  |  | 117 | 117 | 117 |  | 12/1/2013 |  | 15:00 |  |
| LINE 5 (15 KV) |  | 1.53 |  |  |  | 69 | 69 | 69 |  | 30/12/2012 |  | 19:00 |  |
| LINE 6 (15 KV) |  | 1.97 |  |  |  | 89 | 89 | 89 |  | 27/12/2012 |  | 20:00 |  |
| LINE 1 (33 KV) |  | 1.09 |  |  |  | 24 | 24 | 24 |  | 7/1/2013 |  | 16:00 |  |
| LINE 2 (33 KV) |  | 2.45 |  |  |  | 54 | 54 | 54 |  | 14/1/2013 |  | 19:00 |  |
| Minimum Load September 2013 |  |  |  |  |  |  |  |  |  |  | Average/Day Load |  |  |
| Power (MW) | Current (Amp) |  |  |  | Date |  |  |  | Time |  | MW |  | Amp |
|  | R |  | S | T |  |  |  |  |  |  |  |  |  |
| 1.28 | 58 |  | 58 | 58 | 30/12/2013 |  |  |  | 4:00 |  | 5.59 |  | 252 |
| 0.27 | 6 |  | 6 | 6 | 30/1/2013 |  |  |  | 7:00 |  | 1.86 |  | 41 |
| 0.08 | 4 |  | 4 | 4 | 2/1/2013 |  |  |  | 1:00 |  | 0.12 |  | 6 |
| 0.35 | 16 |  | 16 | 16 | 6/1/2013 |  |  |  | 6:00 |  | 0.7 |  | 32 |
| 1.1 | 53 |  | 53 | 53 | 4/1/2013 |  |  |  | 5:00 |  | 2.6 |  | 119 |
| 0.7 | 32 |  | 32 | 32 | 7/1/2013 |  |  |  | 4:00 |  | 1.65 |  | 74.5 |
| 0.17 | 8 |  | 8 | 8 | 27/12/2013 |  |  |  | 9:00 |  | 0.85 |  | 38.5 |
| 0.17 | 8 |  | 8 | 8 | 27/12/2013 |  |  |  | 20:00 |  | 1.07 |  | 48.5 |
| 0.04 | 1 |  | 1 | 1 | 17/1/2013 |  |  |  | 18:00 |  | 0.56 |  | 12.5 |
| 0.27 | 6 |  | 6 | 6 | 13/1/2013 |  |  |  | 7:00 |  | 1.36 |  | 30 |

| Bay / Feeder Name |  | 2013 octobre Peak Load |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Power (MW) |  |  | Current (Amp) |  |  |  |  | Date |  |  | Time |
|  |  |  |  |  | R |  | S | T |  |  |  |  |  |
| TRAF 1 (15 KV) |  | 10.71 |  |  | 482 |  | 842 | 842 |  | 6/3/2013 |  |  | 19:00 |
| TRAF 2 (33 KV) |  | 3.54 |  |  | 78 |  | 78 | 78 |  | 6/3/2013 |  |  | 19:00 |
| LINE 1 (15 KV) |  | 1.31 |  |  | 59 |  | 59 | 59 |  | 5/3/2013 |  |  | 14:00 |
| LINE 2 (15 KV) |  | 1.13 |  |  | 51 |  | 51 | 51 |  | 6/3/2013 |  |  | 19:00 |
| LINE 3 (15 KV) |  | 4.35 |  |  | 196 |  | 196 | 196 |  | 6/3/2013 |  |  | 19:00 |
| LINE 4 (15 KV) |  | 2.62 |  |  | 118 |  | 118 | 118 |  | 6/3/2013 |  |  | 19:00 |
| LINE 5 (15 KV) |  | 1.33 |  |  | 60 |  | 60 | 60 |  | 6/3/2013 |  |  | 19:00 |
| LINE 6 (15 KV) |  | 1.97 |  |  | 89 |  | 89 | 89 |  | 3/3/2013 |  |  | 20:00 |
| LINE 1 (33 KV) |  | 1.09 |  |  | 24 |  | 24 | 24 |  | 9/3/2013 |  |  | 18:00 |
| LINE 2 (33 KV) |  | 2.54 |  |  | 54 |  | 54 | 54 |  | 6/3/2013 |  |  | 19:00 |
| Octobere Minimum Load |  |  |  |  |  |  |  |  |  |  | Average/Day Load |  |  |
| Power (MW) | Current (Amp) |  |  |  |  | Date |  |  | Time |  | MW | Amp |  |
|  | R |  | S | T |  |  |  |  |  |  |  |  |  |
| 1.97 | 89 |  | 89 | 89 |  | 10/3/2013 |  |  | 5:00 |  | 6.34 | 285.5 |  |
| 0.22 | 5 |  | 5 | 5 |  | 2/3/2013 |  |  | 22:00 |  | 1.88 | 41.5 |  |
| 0.17 | 8 |  | 8 | 8 |  | 12/2/2013 |  |  | 17:00 |  | 0.74 | 33.5 |  |
| 0.35 | 16 |  | 16 | 16 |  | 12/2/2013 |  |  | 1:00 |  | 0.74 | 33.5 |  |
| 1.11 | 50 |  | 50 | 50 |  | 29/2/2013 |  |  | 2:00 |  | 2.73 | 123 |  |
| 0.55 | 25 |  | 25 | 25 |  | 19/2/2013 |  |  | 4:00 |  | 1.58 | 71.5 |  |
| 0.17 | 8 |  | 8 | 8 |  | 12/2/2013 |  |  | 23:00 |  | 0.75 | 34 |  |
| 0.11 | 5 |  | 5 | 5 |  | 13/2/2013 |  |  | 10:00 |  | 1.04 | 47 |  |
| 0.22 | 5 |  | 5 | 5 |  | 2/3/2013 |  |  | 12:00 |  | 0.655 | 14.5 |  |
| 0.36 | 8 |  | 8 | 8 |  | 28/2/2013 |  |  | 20:00 |  | 1.45 | 31 |  |

Appendix- B

%***** DILLA GRID CONNECTED MICRO GRID SYSTEM **********

% REACTIVE POWER CONTROLING DURING CONTINGENCY CONDITION  by using ANN

% cells using feed forward, radial basis and recurrent current neural network

%*****kumilachew chane January 2021******

% MATLAB data file given below.

%inputR, targetRP and actual data

% THE reactive power in the point of common coupling RPIPCC.

%reactive power during contingency condition reactivePC

%reactive power during normal condition reactivePN

%reactive power  compensation of the following feeder/traffo

%reactive power compensation by SVC controled by ANN

%reactive power variation  during  contingency of each feeder RPVCF

% existance of the reactive power in pu expression ERPINPU .

% the targeted data will be the compensated reactive power.

nntool

feederN=[1 2 3 4 5 6 7 8 9 ];

inputR[ feeder rate  ];

TRPSVC=[ reactive power of each ];

net = newff(inputR,targetRP, 3);

net.trainParam.epochs=2000;

net.trainParam.goal=0.01;

net = train(net,inputR,targetRP );

COMPENSATIONP = sim(net,inputR);

eg = 0.02;

% sum-squared error goal

sc = 5;

% spread constant

net = newrb(feederN, targetRP,eg,sc);

COMPENSATIONP = sim(net,feederN);

cheek the SVC of ANN,

selecte the rate of max real power feeder,

reed the large reactive power feeder,

%feeder disturbance rate during sever disturbance FDR

FDR=totalFeederrate*0.75*9;

%feeder disturbance rate during au sever disturbance UFDR

UFDR=totalfeederrate*.25*9;

%reactivepower generation due to disturbance RPGD

%total reactive power of the system TRPS

RPGD=TRPS*0.28;

plot(feederN,targetRP,'r');

hold on;

plot(feederN,COMPENSATIONP,'-');

%compensated reactive power value in the SVC

legend('Actual O/P','COMPENSATIONRP O/P');

title('REACTIVE POWER COMPENSATION ANN BASED SVC ') ;

xlabel('feederN ');

ylabel('Load Demand (KVAR)');

cheek the SVC of ANN,

selecte the rate of max real power feeder,

reed the large reactive power feeder,

%feeder disturbance rate during sever disturbance FDR

FDR=totalFeederrate*0.75*9;

%feeder disterbace rate during au sever disturbance UFDR

UFDR=totalfeederrate*.25*9;

%reactivepower generation due to disturbance RPGD

%total reactive power of the system TRPS

RPGD=TRPS*0.28;

reactivePC=(targetRP+0.33*inputR);

reactivePN=(0.50*inputR)

COMPENSATIONRP=132*(.28*9*targetRP)

RPCV=reactivePC-reactivePN

RPCVF=RPCV./(.95*targetRP)

percentofinprovedCRP=((maxRP-minRP)*100)./minRP

CRP=9*(0.85*(0.95*inputR+0.85*targetRP))./(targetRP*.95)

RPIPCC=((targetRP- COMPENSATIONP)*.95)./ targetRP;

ERPINPU= RPIPCC*100;

MAPE=sum(ERPINPU)/9;

disp([feederN' targetRP' COMPENSATIONP'   RPIPCC' ERPINPU' RPCV' RPCVF' CRP'])

% THE reactive power in the point of common coupling RPIPCC.

%reactive power during contingency condition reactivePC

%reactive power during normal condition reactivePN

%reactive power compensation of the following feeder/traffo

%reactive power compensation by SVC controlled by ANN

%reactive power variation during contingency of each feeder RPVCF

% existence of the reactive power in pu expression ERPINPU .

% the targeted data will be the compensated reactive power.

nntool

feederN=[1 2 3 4 5 6 7 8 9 ];

inputR=[  reactive power of a feeder  ];

targetRP=[ reactive power in MVAR of each feeder ];

net = newff(inputR,targetRP, 3);

net.trainParam.epochs=2000;

net.trainParam.goal=0.01;

net = train(net,inputR,targetRP );

COMPENSATIONP = sim(net,inputR);

eg = 0.02;

% sum-squared error goal

sc = 5;

% spread constant

net = newrb(feederN, targetRP,eg,sc);

COMPENSATIONP = sim(net,feederN);

plot(feederN,targetRP,'r');

hold on;

plot(feederN,COMPENSATIONP,'-');

legend('Actual O/P','COMPENSATIONRP O/P');

title('REACTIVE POWER COMPENSATION ANN BASED SVC ') ;

xlabel('feederN ');

ylabel('Load Demand (KVAR)');

reactivePC=(targetRP+0.33*inputR);

reactivePN=(0.50*inputR)

COMPENSATIONRP=132*(.28*9*targetRP)

RPCV=reactivePC-reactivePN

RPCVF=RPCV./(.95*targetRP)

percentofinprovedCRP=((maxR-minR)*100)./minR

CRP=9*(0.85*(0.95*inputR+0.85*targetRP))./(targetRP*.95)

RPIPCC=((targetRP- COMPENSATIONP)*.95)./ targetRP;

ERPINPU= RPIPCC*100;

MAPE=sum(ERPINPU)/9;

disp([feederN' targetRP' COMPENSATIONP'   RPIPCC' ERPINPU' RPCV' RPCVF' CRP'])

%inputR, targetRP and actual data

%the GCMG SYSTEM  active power flow  after compensation APF

% THE SYSTEM REAL POWER IMPROVEMENT after compensation process  API

%IMPROVED POWER FACTORIN THE GCMG SYSTEM IPF

%ACTIVE POWER IN EACH TRAFFO PT

%TOTAL POWER IN THE GCMG SYSTEM TP

% MINIMUM MICRO GRID POWER GENERATION LIMIT of mg power generation LMGPG

nntool

feederN=[1 2 3 4 5 6 7 8 9 ];

inputP=[  active power of a feeder ];

targetIP=[ active power of each feeder in the system  ];

net = newff(inputP,targetIP, 3);

net.trainParam.epochs=2000;

net.trainParam.goal=0.01;

net = train(net,inputP,targetIP );

INPROVED = sim(net,inputP);

eg = 0.02;

% sum-squared error goal

sc = 5;

% spread constant

net = newrb(feederN, targetIP,eg,sc);

INPROVED = sim(net,feederN);

plot(feederN,targetIP,'r');

hold on;

plot(feederN,INPROVED,'-');

legend('Actual O/P','INPROVED O/P');

title('ACTIVE  POWER INPROVED  BASED ON RPC ANN BASED SVC ') ;

xlabel('feederN ');

ylabel('Load Demand (KW)');

activePC=(targetIP+0.23*inputP);

INPROVED=132*(.23*9*targetIP)

APCVF=RPCV./(.95*targetRP)

activePF=activePC./(.95*targetIP)

percentofinprovedCAP=((max-min)*100)./min

CAP=9*(0.85*(0.95*inputP+0.85*targetIP))./(targetIP*.95) APIPCC=((targetIP-INPROVED)*.95)./ targetIP;

ERPINPU= RPIPCC*100;

MAPE=sum(ERPINPU)/9;

disp([feederN' targetIP' INPROVED'])

APPENDIX -C

LOAD FLOW AND LOSS REPORT FOR GCMG SYSTEM

APPENDIX -D

Fig  a) Neural network tanning  of the system with the neural network structure and  Fig b)of Gradient training unit and validation of the ANN of SVC in the NN train tool

Fig a)                                                                                                                  fig b)

Fig a) of Validation indication and  fig b) ANN result indicator for  train  ,validation and test of the ANN controller of the neural neuron surface

Fig a)  Simulink of system frequency improvement by using ILFC system  and fig b)  Simulink of feeder rate and power flow continuity of the system

Simulink of General system and sub system of MG in the mat lab Simulink surface

Simulink of Grid connected PV system in the mat lab Simulink surface

Mat lab Simulink of Battery charge controller  and  storage system in the MG system

Grid connected micro grid system  with fuzzy  based  SVC controller